SSS – GENERIC SERVER AND NETWORK CABINET

System Segment Specification

Generic Server and Network Cabinet

Generic

| APPROVAL |  |  |
| --- | --- | --- |
|  | Name and Role/Job Title | Esignature |
| Written by | Natalia Karmatska RM Anatol Amon HW WPM |  |
| Verified by | Ramy Al Ali QAM |  |
| Approved by | Dieter Baumgartner PDA HW Michael Franzl ARC |  |

| LOG OF CHANGES |  |  |  |
| --- | --- | --- | --- |
| Revision | Date | Author | Change Description |
| 01 | 2023-03-23 | Bernhard Mandl | First release |
| 02 | 2023-07-21 | Bernhard Mandl | Requirements Update |
| 03 | 2024-02-28 | Bernhard Mandl | See chapter 1.5.3 |
| 04 | 2025-03-10 | Bernhard Mandl | See chapter 1.5.4 |
| 05 | 2026-07-10 | Natalia Karmatska | See chapter 1.5.5 |

Contents

1.	Scope	6

1.1	Identification	6

1.2	System overview	6

1.3	Document overview	6

1.4	Intended audience	7

1.5	Evolution of the document	7

1.5.1	Edition 01	7

1.5.2	Edition 02	7

1.5.3	Edition 03	8

1.5.4	Edition 04	9

1.5.5	Edition 05	10

1.6	Terms, Abbreviations and Acronyms	13

1.7	Types of Requirements	14

1.8	Requirements Attributes	15

1.9	Information about Document Creation	16

2.	References and Terms	18

2.1	Referenced Documents	18

2.2	Standards and Procedures	19

3.	Issues, decisions and justifications	22

4.	Requirements	35

4.1	General Requirements	35

4.2	Operational Requirements	36

4.3	Physical Requirements	44

4.4	Environmental Requirements	54

4.5	Safety	60

4.6	Physical Security	62

4.7	Cyber Security	63

4.8	Dependability Requirements	65

4.9	Industrialization	75

4.10	Product Safety	77

4.11	Performance	83

4.12	Technical Requirements	85

4.13	Functional Requirements	87

4.14	Open Issue	89

APPENDIX A	index of requirements	91

List of Tables

Table 1	Project Identification	6

Table 2	Security / Maturity Level	6

Table 3	Terms, Abbreviations and Acronyms	13

Table 4	Types of Requirements	14

Table 5	Requirements Attributes	15

Table 6	Information about Document Creation	17

Table 7	Referenced Documents	18

Table 8	Standards and Procedures	19

List of Figures

No table of figures entries found.

# Scope

## Identification

This IPS-HW specification has been established in accordance with the Systems Engineering Management Plan [SEMP] and the Work Package Description [WPD], which collectively provide the structured framework for the planning, execution, and management of the project.

Table 1	Project Identification

| Project | 100025795 - ATRELDE91 DSTW ÖBB Entwicklung |
| --- | --- |
| Solution | IPS |
| Contract | n.a. |
| Customer | OMC 3.0 + ELEKTRA 4.0 + SCWS Geored. |
| End User | Generic |
| SIL Level | Non-safety-related |

Table 2	Security / Maturity Level

| Security Level | SL-C 2 |
| --- | --- |
| Maturity Level | ML 2 |

## System overview

The configuration of the generic server cabinet and the generic network cabinet is based on the concept of the infrastructure platform of the geo-redundant systems [OMC-3.x SSDD], [SB_Concept], [Tech_Concept] which utilizes COTS industrial servers and in a modular and scalable setup.

Regarding one location, this concept consists of three identical and redundant server cabinets and one network cabinet as a central connection point for the server cabinets as well as for connection with peripheral systems, including the systems at the geo-redundant counterpart location.

## Document overview

This IPS-HW specification has been established in accordance with the Systems Engineering Management Plan [SEMP] and the Work Package Description [WPD], which collectively provide the structured framework for the planning, execution, and management of the project.

This document contains the HW requirements for the Generic Server Cabinet, the Generic Network Cabinet, based on the OMC related requirements [OMC 3.0 SSS] and DIL related requirements [DIL SSS] for the cabinets.

In this document, “Rack” means the shelf inside the cabinet, where the components are assembled. So, the cabinet contains the rack/shelf with the assembled equipment.

## Intended audience

The target audience of this document includes:

- Product Line Architect (PLA)

- Product Line Manager (PLM)

- System Engineering Manager (SEM)

- System Architect (ARC)

- Project Security Manager

- RAM Assurance Manager (RAM-AM)

- Industrialization Manager (IM)

- IVVQ Manager (IVVQM)

- Verifier (VER)

- Validator (VAL)

- Quality Assurance Manager (QAM)

- Hardware Engineering Manager (HwEM)

## Evolution of the document

A new edition is to be distributed to the group of readers defined in the previous section.

All editions of this document are version-managed in the documentation archive of Hitachi Rail Austria.

### Edition 01

Initial Edition

### Edition 02

Update of Identification

Update of Norms:

EN 61000-6-2 & EN 61000-6-4

Update of Requirements:

GENCAB:HW-SSS:REQ:0001; GENCAB:HW-SSS:REQ:0002; GENCAB:HW-SSS:REQ:0003; GENCAB:HW-SSS:REQ:0004; GENCAB:HW-SSS:REQ:0064; GENCAB:HW-SSS:REQ:0087; GENCAB:HW-SSS:REQ:0076; GENCAB:HW-SSS:REQ:0077; GENCAB:HW-SSS:REQ:0101; GENCAB:HW-SSS:REQ:0102; GENCAB:HW-SSS:REQ:0103; GENCAB:HW-SSS:REQ:0104

– Comment added

GENCAB:HW-SSS:REQ:0003; GENCAB:HW-SSS:REQ:0004; GENCAB:HW-SSS:REQ:0008; GENCAB:HW-SSS:REQ:0054; GENCAB:HW-SSS:REQ:0058; GENCAB:HW-SSS:REQ:0063; GENCAB:HW-SSS:REQ:0064; GENCAB:HW-SSS:REQ:0067; GENCAB:HW-SSS:REQ:0075; GENCAB:HW-SSS:REQ:0076; GENCAB:HW-SSS:REQ:0077; GENCAB:HW-SSS:REQ:0085; GENCAB:HW-SSS:REQ:0088; GENCAB:HW-SSS:REQ:0089; GENCAB:HW-SSS:REQ:0090; GENCAB:HW-SSS:REQ:0091; GENCAB:HW-SSS:REQ:0092; GENCAB:HW-SSS:REQ:0093; GENCAB:HW-SSS:REQ:0094; GENCAB:HW-SSS:REQ:0096; GENCAB:HW-SSS:REQ:0101; GENCAB:HW-SSS:REQ:0102; GENCAB:HW-SSS:REQ:0103; GENCAB:HW-SSS:REQ:0104

– Requirements text and/or comment text changed

GENCAB:HW-SSS:REQ:0113; GENCAB:HW-SSS:REQ:0114; GENCAB:HW-SSS:REQ:0115; GENCAB:HW-SSS:REQ:0116

– New requirements

GENCAB:HW-SSS:REQ:0009 – Link to one requirement deleted

GENCAB:HW-SSS:REQ:0082 – Origin changed

GENCAB:HW-SSS:REQ:0001; GENCAB:HW-SSS:REQ:0002; GENCAB:HW-SSS:REQ:0087; GENCAB:HW-SSS:REQ:0107; GENCAB:HW-SSS:REQ:0108; GENCAB:HW-SSS:REQ:0109; GENCAB:HW-SSS:REQ:0024; GENCAB:HW-SSS:REQ:0081; GENCAB:HW-SSS:REQ:0090; GENCAB:HW-SSS:REQ:0115

– IDJ link added

GENCAB:HW-SSS:REQ:0090; GENCAB:HW-SSS:REQ:0115

– Priority changed

Update IDJ:

GENCAB:HW-SSS:IDJ:ID:0006; GENCAB:HW-SSS:IDJ:ID:0007; GENCAB:HW-SSS:IDJ:ID:0008; GENCAB:HW-SSS:IDJ:ID:0009; GENCAB:HW-SSS:IDJ:ID:0010; GENCAB:HW-SSS:IDJ:ID:0011; GENCAB:HW-SSS:IDJ:ID:0012

– new IDJ

GENCAB:HW-SSS:IDJ:ID:0003 – IDJ text changed

### Edition 03

Template changed

Table 2 added

Chapter Cyber Security added

Update of Norms:

EN 50124-1, EN 50125-3, EN 50129, EN 60529, EN 60664-1, EN 60721-3-2, EN 60529, EN 60721-3-2, EN 60721-3-3, EN 61000-6-2, EN 61000-6-4, EN 61010-1, EN 62368-1, EN 60332-1-2, EN 60332-2-2, EN IEC 60332-3-24

EN 50121-4 added

EN IEC 62443-4-2 added

Update of Referenced Documents:

ELEKTRA Environmental Conditions added

ÖBB IKT-Sicherheitsrichtlinie added

DSTW Anforderungen Analyse added

new edition of OMC 3.0 SSS

Update IDJ:

[GENCAB:HW-SSS:IDJ:0001] - new maximum cabinet size of 800mm x 1200mm x 2100mm

[GENCAB:HW-SSS:IDJ:0004] - IDJ deleted

[GENCAB:HW-SSS:IDJ:0005] - IDJ deleted

[GENCAB:HW-SSS:IDJ:0006] - Text and Decision updated

Update of Requirements:

[GENCAB:HW-SSS:REQ:0006] - Update of comment

[GENCAB:HW-SSS:REQ:0012] - cabinet size changed

[GENCAB:HW-SSS:REQ:0024] - Verification Step changed

[GENCAB:HW-SSS:REQ:0028] - Link to Top Level requirement and comment added

[GENCAB:HW-SSS:REQ:0059] - added reference to [EN 50121-4] and added comment

[GENCAB:HW-SSS:REQ:0063] - Link to IDJ:0004 deleted and text changed

[GENCAB:HW-SSS:REQ:0064] - Link to IDJ:0005 deleted and text changed

[GENCAB:HW-SSS:REQ:0077] - Verification Step changed

[GENCAB:HW-SSS:REQ:0087] - Text and comment changed

[GENCAB:HW-SSS:REQ:0088] - Verification Step changed

[GENCAB:HW-SSS:REQ:0089] - Verification Step changed

[GENCAB:HW-SSS:REQ:0090] - Verification Step changed

[GENCAB:HW-SSS:REQ:0091] - Verification Step changed

[GENCAB:HW-SSS:REQ:0092] - Verification Step changed

[GENCAB:HW-SSS:REQ:0093] - Verification Step changed

[GENCAB:HW-SSS:REQ:0094] - Verification Step changed

[GENCAB:HW-SSS:REQ:0095] - Verification Step changed

[GENCAB:HW-SSS:REQ:0096] - Verification Step changed

[GENCAB:HW-SSS:REQ:0097] - Verification Step changed

[GENCAB:HW-SSS:REQ:0098] - Verification Step changed

[GENCAB:HW-SSS:REQ:0099] - Verification Step changed

[GENCAB:HW-SSS:REQ:0100] - cabinet size changed

[GENCAB:HW-SSS:REQ:0117] - new requirement

[GENCAB:HW-SSS:REQ:0118] - new requirement

### Edition 04

New Template

Important Note:

The number 3BU 16000 0002 DTAPA is checked into DWF. The identifier 3BU 16000 0002 305EN is valid for SharedPalma.

Solution changed

Table 5: IEC description added

Referenced Documents changed:

Table 7: Hazard Rate Elektra 2.x document updated

EoC - Reference Hardware COTS Server vs. TAS Platform Core SRACS added

ÖBB IKT-Sicherheitsrichtlinie deleted

OMC 3.x Low Level Design

New Requirements:

[GENCAB:HW-SSS:REQ:0119] - Secure Boot

[GENCAB:HW-SSS:REQ:0120] - Configuration Interface

Update of requirements:

[GENCAB:HW-SSS:REQ:0001] - Link to Top-Level requirement added

[GENCAB:HW-SSS:REQ:0002] - Link to Top-Level requirement added

[GENCAB:HW-SSS:REQ:0006] - Requirements text and comment changed

[GENCAB:HW-SSS:REQ:0008] - Verification Method changed

[GENCAB:HW-SSS:REQ:0009] - Links to Top-Level requirement changed

[GENCAB:HW-SSS:REQ:0011] - Links to Top-Level requirement changed

[GENCAB:HW-SSS:REQ:0031] - Verification Method and Verification Step changed

[GENCAB:HW-SSS:REQ:0044] - Link to Top-Level requirement changed

[GENCAB:HW-SSS:REQ:0075] - Requirements text and comment text changed

[GENCAB:HW-SSS:REQ:0077] - Verification Method and Verification Step changed

[GENCAB:HW-SSS:REQ:0080] - Comment text changed

[GENCAB:HW-SSS:REQ:0081] - Verification Method and Verification Step changed

[GENCAB:HW-SSS:REQ:0083] - Requirements text and links to Top-Level requirement changed

[GENCAB:HW-SSS:REQ:0084] - Link to Top-Level requirement added, Security mapping added

[GENCAB:HW-SSS:REQ:0085] - Link to Top-Level requirement added, Security mapping added

[GENCAB:HW-SSS:REQ:0086] - Verification Method and Verification Step changed

[GENCAB:HW-SSS:REQ:0088] - Verification Method changed

[GENCAB:HW-SSS:REQ:0089] - Verification Method changed

[GENCAB:HW-SSS:REQ:0090] - Verification Method changed

[GENCAB:HW-SSS:REQ:0091] - Verification Method changed

[GENCAB:HW-SSS:REQ:0092] - Verification Method changed

[GENCAB:HW-SSS:REQ:0093] - Verification Method changed

[GENCAB:HW-SSS:REQ:0094] - Verification Method changed

[GENCAB:HW-SSS:REQ:0095] - Verification Method changed

[GENCAB:HW-SSS:REQ:0096] - Verification Method changed

[GENCAB:HW-SSS:REQ:0097] - Verification Method changed

[GENCAB:HW-SSS:REQ:0098] - Verification Method changed

[GENCAB:HW-SSS:REQ:0099] - Verification Method changed

[GENCAB:HW-SSS:REQ:0100] - Verification Step changed

[GENCAB:HW-SSS:REQ:0110] - Link to Top-Level requirement added, Security mapping added

[GENCAB:HW-SSS:REQ:0118] - Requirements Title changed, Type changed to FUR and moved to chapter Functional Requirements

### Edition 05

The specification has been updated to incorporate new top-level requirements introduced by the Digital Interlocking [DIL] project, in accordance with the [DIL SSS]

Update of chapters:

Update of chapter 1.1 Identification

Update of chapter 1.2 System overview

Update of chapter 1.3 Document overview

Update of chapter 1.6 Terms, Abbreviations and Acronyms

Update of chapter 2 References and Terms

Update of chapter 3 Issues, decisions and justifications: links to the EL4 IDJ-RA module are introduced

Update of chapter 4 Requirements

New requirements:

[GENCAB:HW-SSS:REQ:0121] -  Automatic Start-up of HW components

[GENCAB:HW-SSS:REQ:0122] -  Minimum Useful Life - Continuous Utilization

[GENCAB:HW-SSS:REQ:0123] -  Fulfillment of Standard EN 50126

[GENCAB:HW-SSS:REQ:0124] -  Maintainability and Maintenance - Component Replacement - Approved Tools

[GENCAB:HW-SSS:REQ:0125] -  Safety - Maintenance – SRACs - > to be descoped

[GENCAB:HW-SSS:REQ:0126] -  Safety - Maintenance – Activities - > to be descoped

[GENCAB:HW-SSS:REQ:0127] -  Safety - Maintenance - Exchange of elements - > to be descoped

[GENCAB:HW-SSS:REQ:0128] -  Server Hardware - Minimum Installation Depth

[GENCAB:HW-SSS:REQ:0129] -  Network & Transmission Technology - [SiDiNet] and [DN2020]

[GENCAB:HW-SSS:REQ:0130] -  Network & Transmission Technology - Network Cabling

[GENCAB:HW-SSS:REQ:0131] -  Grounding and Surge Protection - Grounding Concept

[GENCAB:HW-SSS:REQ:0132] -  Grounding and Surge Protection

[GENCAB:HW-SSS:REQ:0133] -  Reliability - Replacement of HW Component - No operational Impact - > to be descoped

[GENCAB:HW-SSS:REQ:0134] -  Maintainability and Maintenance - Spare Parts Storage - Concept

[GENCAB:HW-SSS:REQ:0135] -  Maintainability and Maintenance - Spare Parts Storage - Information

[GENCAB:HW-SSS:REQ:0136] -  Maintainability and Maintenance - Spare Parts Storage – Effort - > to be descoped

[GENCAB:HW-SSS:REQ:0137] -  Maintainability and Maintenance - Spare Parts Storage - Maintenance

[GENCAB:HW-SSS:REQ:0138] -  Power Supply - Non-Availability related Components - Monitoring and Backup

[GENCAB:HW-SSS:REQ:0139] -  Server distribution

[GENCAB:HW-SSS:REQ:0140] -  Split-brain - connection between HW components

[GENCAB:HW-SSS:REQ:0141] -  Split-brain - connection between HW components & Geointerconnection

[GENCAB:HW-SSS:REQ:0142] -  Cooling Concept – Cabinet

[GENCAB:HW-SSS:REQ:0143] - Maintainability and Maintenance - Labelling – Units - > to be descoped

[GENCAB:HW-SSS:REQ:0144] - Double doors

[GENCAB:HW-SSS:REQ:0145] - Minimum Useful Life - COTS Components

[GENCAB:HW-SSS:REQ:0146] - Minimum supply period - spare parts

[GENCAB:HW-SSS:REQ:0147] - Power Supply - PDUs

Modified requirements:

[GENCAB:HW-SSS:REQ:0049] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description” updated

[GENCAB:HW-SSS:REQ:0088] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description”, “Comments” updated

[GENCAB:HW-SSS:REQ:0012] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description” updated

[GENCAB:HW-SSS:REQ:0107] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0077] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description” updated

[GENCAB:HW-SSS:REQ:0082] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description”, “Comments” updated

[GENCAB:HW-SSS:REQ:0027] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description” updated, “Synopsys ”updated.

[GENCAB:HW-SSS:REQ:0028] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description” updated, “Synopsys ”updated.

[GENCAB:HW-SSS:REQ:0085] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “see also” updated

[GENCAB:HW-SSS:REQ:0086] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description”, “Synopsis” updated

[GENCAB:HW-SSS:REQ:0071] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0084] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated, “Description” updated

[GENCAB:HW-SSS:REQ:0110] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0083] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0044] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description” updated

[GENCAB:HW-SSS:REQ:0046] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0011] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0008] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0080] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Verification Method”, “Verification Step” updated, status changed to “to be descoped”

[GENCAB:HW-SSS:REQ:0081] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0031] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0075] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description”, “Verification Method”, “Verification Step” updated

[GENCAB:HW-SSS:REQ:0118] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", "Description", “Comments” updated

[GENCAB:HW-SSS:REQ:0119] - Attribute "TA See also" updated

[GENCAB:HW-SSS:REQ:0060] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0059] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0077] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description” updated

[GENCAB:HW-SSS:REQ:0070] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0057] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0098] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0099] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0063] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0101] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0102] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0087] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0010] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0106] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0051] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0050] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0078] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0095] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Comments” updated

[GENCAB:HW-SSS:REQ:0097] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0024] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release", “Description” updated

[GENCAB:HW-SSS:REQ:0113] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0114] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0115] - Links to Top-Level [DIL] requirement added, Attributes "TA Target release" updated

[GENCAB:HW-SSS:REQ:0076] -  Attribute “Comments” updated

[GENCAB:HW-SSS:REQ:0006] -  Attribute “Comments” updated

[GENCAB:HW-SSS:REQ:0100] -  Attribute “Description” updated

[GENCAB:HW-SSS:REQ:0014] -  Attribute “Description” updated

[GENCAB:HW-SSS:REQ:0065] -  Attribute “Description” updated

[GENCAB:HW-SSS:REQ:0067] -  Attribute “Description” updated

[GENCAB:HW-SSS:REQ:0089] -  Attribute “Description” updated

[GENCAB:HW-SSS:REQ:0090] -  Attribute “Description” updated

Linkset:

The evidence of compliance links has been changed to reference new source: OMC/OMC Security

## Terms, Abbreviations and Acronyms

For the list of used acronyms based on OMC & DIL related definitions and terms, see [OMC Glossary], EL_GLOSS.

Table 3	Terms, Abbreviations and Acronyms

| BFZ | Betriebsführungszentrale |
| --- | --- |
| BMC | Base Management Controller |
| BOS | Operating System (Betriebs-Operationssystem) |
| COTS | Commercial Off The Shelf |
| DWF | Document Web Frontend |
| DIL | Digital Interlocking |
| EBO | Uniform Operator Interface (Einheitliche Bedienoberfläche) |
| HSE | Health, Safety and Environment |
| HW | Hardware |
| IDJ | Issue/Decision/Justification |
| IPS | Integrated Platform Services |
| KVM | Keyboard Video Mouse |
| LRU | Least Replaceable Unit |
| MRT | Mean repair time |
| OMC | Operation Management Center |
| PDU | Power Distribution Unit |
| REACH | Registration, Evaluation, Authorization and Restriction of Chemicals |
| RoHS | Restriction of Hazardous Substances |
| SSS | System Subsystem Specification |
| ToR | Top of Rack (switch) |
| UPS | Uninterruptible Power Supply |
| VIL | Virtual Interlocking |
| WEEE | Waste Electrical and Electronic Equipment |

Terms and Definitions are provided below (non-exhaustive list)

| Availability Zone | One of the three groups of server racks at a site, connected via highly available network and used for the redundant distribution of the application instances and infrastructure resources. |
| --- | --- |
| Balanced distribution | A distribution of k items to n buckets is called balanced if the number of items per bucket differs by at most 1. |
| IDJ | A structured record used to document project-related issues, decisions and justifications, which ensures traceability of decision-making and provides rationale for chosen solutions throughout the project lifecycle |
| Geo-redundancy | A system design approach that distributes critical components, data or infrastructure across multiple geographic locations (Datacenters) to ensure availability, fault tolerance, and disaster recovery in case of one location (Datacenter) failure |
| Facilities | Additional spaces, rooms, or areas provided for use or support. |

## Types of Requirements

Table 4	Types of Requirements

| CSR | Customer Specifics Requirement |
| --- | --- |
| DAT | Data Requirement |
| DOR | Documentation Requirement |
| DPR | Dependability Requirement |
| ECR | Environmental Conservation Requirement |
| FUR | Functional Requirement |
| GCR | General Constraints Requirement |
| MCR | Management and Commercial Requirement |
| MDR | Maintenance and Diagnosis Requirement |
| MIR | Man-Machine Interface Requirement |
| MPR | Manufacturing and Production Requirement |
| OAR | Operational Aliveness Requirement |
| PER | Physical/Environmental Requirement |
| PHR | Prevention of Hazards Requirement |
| PRR | Performance and Real-Time Requirement |
| PSR | Product Startup Requirement |
| RSR | Resource Support and Consumption Requirement |
| SAR | Safety Requirement |
| SCR | Supplier to Customer Requirement |
| SER | Security Requirement |
| TCR | Tool Chain Requirement |
| TIR | Technical Interface Requirement |
| TVR | Testing and Validation Requirement |

## Requirements Attributes

Table 5	Requirements Attributes

| Identifier | Unique identifier of the requirement. |
| --- | --- |
| Category | Category (Type) of Requirement → see Ch.0 |
| Synopsis | Unique short description of the requirement. |
| Description | Detailed description of the requirement. |
| Status | Status of the requirement. Possible values: draft requirement is collected and written down, not approved approved requirement is approved, reviewed by all affected groups in negotiation requirement is still under construction, relevant inputs are missing to be descoped requirement is planned to be delayed to a later release descoped requirement is delayed to a later release to be deleted requirement is planned to be deleted, no formal approval for deletion yet. deleted requirement is no longer valid and will not be implemented at all |
| Origin | Link to referenced generic requirements based on the OMC overall system SSS [OMC 3.0 SSS] (related to OMC Feature List [FL]), DIL overall system SSS [DIL SSS], DIL Feature List [DIL FL], or the link to the IDJ (information about decisions concerning the requirement, which were made during workshops or comparable meetings / mails). |
| Priority | Priority of implementing the requirement. One of the following values can be used for each requirement: Mandatory Implementation is obligatory Optional Improvement of the product. May be implemented later and the acceptance is not influenced by the absence of the implementation. |
| Target Release | The first attribute value with the lowest number indicates the first baseline (target release) in which the requirement was first released. Further attribute values with higher numbers indicate baselines in which the requirement was content wise changed. |
| Stability | Expected stability of the requirement over the whole life cycle of the system. Possible values: stable: will probably not be changed during the product life cycle volatile: changes are expected instable: frequent changes are expected |
| Originator | Trigger of the requirement. Possible values: Customer, Product Management, Product Strategy, RAM, Safety, Quality, Technics (R&D), Standards/Legal, Equipment Practice. |
| Cabinet | Cabinet type for which the requirement applies. Possible values: Network cabinet: requirement only applies to the network cabinet Server cabinet: requirement only applies to the server cabinet Generic: requirement applies to both cabinets |
| Verification Method | Coarse verification method of the requirement. Possible values: - Inspection/Review, Analysis, Demonstration, Test. |
| Verification Step | Detailed verification method of the requirement, e.g.: - Safety Analysis, Review, Design Review, Module Test, Integration Test, System test, Qualification Test, RAM Analysis, ... |
| IEC | Link to IEC requirement |
| Comments | Additional information about the requirement |

## Information about Document Creation

The present document was generated using IBM™ Rational DOORS database.

Used settings:

Table 6	Information about Document Creation

| DOORS/RMF Version: | 9.6.1.6/v6.1.0.8 |
| --- | --- |
| DOORS/RMF Module Name: | GENCAB-HW-SSS-Helper |
| DOORS/RMF Module Version (Baseline): | 4.0 |
| DOORS/RMF Module Path: | /Hardware Engineering/Specification |
| DOORS/RMF Export View: | WEXP SSS 0002 DIL |
| DOORS/RMF Current Filter: | (Absolute Number == 48) OR ((Absolute Number == 20) OR (Absolute Number == 12)) |
| DOORS/RMF Export Options 1: | 2,false,2,2,true,false,0,true,false, |
| DOORS/RMF Export Options 2: | true,false,true,2,false,false,true,PostprocessAllStyles,, |
| DOORS/RMF Export Options 3: | ,false,true,false,false,false,true,0,false,4, |
| DOORS/RMF Export Options 4: | 3,###,===,true,false,false,false,false, |
| DOORS Document Template Name: | \\Thales-AT-Data\Thales-AT\PROJECTS\ReqMng\DOORS\Word Export\DOORS-EXPORT-TEMPLATES\IPS-Solution\SRS\SSS IPS HW\3BU_16000_0002_DTAPA_Template_IDJ_new.doc |
| Documentation-Vob Template Name: | 3BU_16000_0002_DTAPA-Template.doc |

# References and Terms

## Referenced Documents

Table 7	Referenced Documents

| Id | Reference |
| --- | --- |
| ELEKTRA Environmental Conditions | Umgebungsbedingungen ELEKTRA 2.x – Entwicklungsvorgaben 3BU 15000 5062 EDAPC, Ed. 08 |
| Industrialisierungsvorgaben | Industrialisierungsvorgaben 3BU 00600 0021 DSAPC, Ed. 03 |
| ÖBB IKT-Sicherheitsrichtlinie | Richtlinie für die Implementierung von IKT-Systemen in Eisenbahn-Infrastrukturanlagen, Version 1c vom 13.03.2018 3BU 51500 1167 DSAPC, Ed. 02 RR |
| DSTW Anforderungen Analyse | DSTW_Anforderungen_Analyse EL-SYS-23-513, Ed. 01 |
| EoC Server | Evidence of Compliance - Reference Hardware COTS Server vs. TAS Platform Core SRACS 3BU 16000 0007 DUAPA, Ed. 01 |
| PACK_INSTR | Verpackungsanweisung - Schrank 8AK 00038 3030 MBAPC, Ed. 01 |
| HSE Instruction | Project/Product HSE Plan BFZ 3.x 3BU 51500 2102 EWAPA Ed. 01 |
| Generic HW Standards | Generic HW Product Safety Standards 3BU 15000 5320 DTAPA, Ed. to be released |
| FL | Feature List - Betriebsführungszentrale 3BU 51500 1002 FLAPC, Ed. 20 |
| DIL FL | Feature List DSTW 3BU 17300 0000 FLAPC Ed.01 Pd.01 |
| OMC 3.0 SSS | System Requirements Specification OMC 3.0 3BU 51500 2010 DTAPQ Ed. 03 |
| BFZ Low Level Design | OMC 3.x Low Level Design 3BU 51500 2055 EDAPA, Ed. 02 |
| SEMP | System Engineering Management Plan (SEMP) IPS Solution - Digital Interlocking OBB 3BU 17300 2001 DPAPA Ed. 01 |
| WPD | Work Package Description (WPD) IPS HW - IPS Solution 3BU 17300 2175 ADAPA Ed. 01 |
| DIL SSS | System Requirements Specification - Digital Interlocking OBB (DIL) - General Requirements 3BU 17300 1251 DTAPA, Ed.02 Pd.01 System Requirements Specification - Digital Interlocking OBB (DIL) - Central Unit Part 1 3BU 17300 1255 DTAPA, Ed.02 Pd.01 System Requirements Specification - Digital Interlocking OBB (DIL) - RAMS 3BU 17300 1257 DTAPA, Ed.02 Pd.01 System Requirements Specification - Digital Interlocking OBB (DIL) - Data Center & Networks 3BU 17300 1258 DTAPA, Ed.02 Pd.01 |
| SB_Concept | Split - Brain avoidance – Technical Concept 3BU 15000 6851 DSAPA Ed.01 (planned) |
| Tech_Concept | Digitales Stellwerk - Technische Konzepte 3BU 17300 0010 DSAPC, Ed.04 |
| OMC Glossary | Glossar BFZ / Glossary OMC 3BU 51500 1037 WDAPQ, Ed. 02 |
| EL_GLOSS | Glossary: Definitions, Acronyms and Abbreviations - ELEKTRA 2.x System, 3BU 15000 0081 DCAPA, Ed. 06 |
| OMC-3.x SSDD | System Segment Design Document OMC 3.x 3BU 51500 2011 DSAPA, Ed. 01 |
| Sicherheitsnachweis ILP | Sicherheitsnachweis, OMC Component ILP 3BU 51500 3015 DUAPC Ed. 09 |
| Rechnerschrank D6 Generisch | Bestückungszeichnung Rechnerschrank D6 Generisch 3BU 15583 AAAA BGAPC, Ed. 16 |
| ELEKTRA 2.x Schrank | Beschreibung, Schrank RAL9002 600x600x2000 Kabeleinführung unten u. oben, mit Dachlüfter 3JA 69010 BBAA DSEGC, Ed. 02 |
| Hazard Rate Elektra 2.x | Elektra 2.X Generisch, Systemsicherheitsnachweis 3BU 15000 5199 DUAPC Ed. 10 |

## Standards and Procedures

Table 8	Standards and Procedures

| Id | Reference |
| --- | --- |
| EN 50121-4 | EN 50121-4:2016 + A1:2019 (OVE EN 50121-4:2017 + A1:2020) Electromagnetic compatibility – Emission and immunity of the signalling and telecommunications apparatus |
| EN 50122 | EN 50122-1:2011 +A1:2011 +AC:2012 +A2:2016 +A3:2016 +A4:2017 Railway applications - Fixed installations - Electrical safety, earthing and the return circuit |
| EN 50124-1 | EN 50124-1:2017 (OVE EN 50124-1:2018 + AC:2023) Railway applications - Insulation coordination - Part 1: Basic requirements - Clearances and creepage distances for all electrical and electronic equipment |
| EN 50125-3 | EN 50125-3:2003 + AC:2010 (ÖVE/ÖNORM 50125-3:2003 + AC:2010) Railway applications - Environmental conditions for equipment - Part 3: Equipment for signalling and telecommunications |
| EN 50126-1 | EN 50126-1:2017 (OVE EN 50126-1:2018) Railway Applications – The Specification and Demonstration of Reliability, Availability, Maintainability and Safety (RAMS) – Part 1: Generic RAMS Process |
| EN 50126-2 | EN 50126-2:2017 (OVE EN 50126-2:2018) Railway Applications – The Specification and Demonstration of Reliability, Availability, Maintainability and Safety (RAMS) – Part 2: Systems Approach to Safety |
| EN 50129 | EN 50129:2018 + AC:2019 (OVE EN 50129:2019) Railway applications – Communication, signalling and processing systems – Safety related electronic systems for signalling |
| EN 50159 | EN 50159:2010 + A1:2020 (ÖVE/ÖNORM EN 50159:2011 + A1:2020) Railway applications - Communication, signalling and processing: Safety-related communication in transmission systems |
| EN 60529 | EN 60529:1991 + AC:1993 + A1:2000 + A2:2013 + AC:2016 + AC:2019 (ÖVE/ÖNORM EN 60529:2014-11 + AC:2017 + AC2:2019) Degrees of protection provided by enclosures (IP Code) |
| EN 50310 | EN 50310:2016+A1:2020 - Telecommunications bonding networks for buildings and other structures - 2020-05-03 |
| EN 60664-1 | IEC 60664-1:2020 + AC:2020 (OVE EN IEC 60664-1:2022) Insulation coordination for equipment within low-voltage supply systems -Part 1: Principles, requirements and tests |
| EN 60721-3-1 | EN IEC 60721-3-1:2018 (OVE EN IEC 60721-3-1:2019) Classification of environmental conditions Part 3-1: Classification of groups of environmental parameters and their severities - Storage |
| EN 60721-3-2 | EN IEC 60721-3-2:2018 + AC:2018 + AC:2022 (OVE EN 60721-3-2:2019 + AC:2023) Classification of environmental conditions Part 3-2: Classification of groups of environmental parameters and their severities Transportation (IEC 104/710/CDV) |
| EN 60721-3-3 | EN IEC 60721-3-3:2019 (OVE EN IEC 60721-3-3:2020) Classification of environmental conditions – Part 3-3: Classification of groups of environmental parameters and their severities – Stationary use at weather protected locations |
| EN 61000-6-2 | EN 61000-6-2:2019 (OVE EN IEC 61000-6-2:2019) Elektromagnetische Verträglichkeit (EMV) Teil 6-2: Fachgrundnormen -Störfestigkeit für Industriebereiche |
| EN 61000-6-4 | EN 61000-6-4:2019 (OVE EN IEC 61000-6-4:2020) Electromagnetic compatibility (EMC) – Part 6-4: Generic standards – Emission standard for industrial environments |
| EN 61010-1 | EN 61010-1:2010 + A1:2019 + AC:2019 (OVE EN 61010-1:2020 + AC:2022 + AC2:2023) Sicherheitsbestimmungen für elektrische Mess-, Steuer-, Regel- und Laborgeräte -Teil 1: Allgemeine Anforderungen |
| EN 62368-1 | EN IEC 62368-1:2020 + A11:2020 + AC:2020 (OVE EN IEC 62368-1:2021 + AC:2023 + AC2:2023) Einrichtungen für Audio/Video-, Informations- und Kommunikationstechnik -Teil 1: Sicherheitsanforderungen / Audio/video, information and communication technology equipment -Part1: Safety requirements |
| EN 60332-1-2 | EN 60332-1-2:2004 + A11:2016 + A12:2020 + A1:2015 (OVE EN 60332-1-2:2022) Tests on electric and optical fibre cables under fire conditions - Part 1-2: Test for vertical flame propagation for a single insulated wire or cable – Procedure for 1 kW pre-mixed flame |
| EN 60332-2-2 | EN 60332-2-2:2004 (ÖVE/ÖNORM EN 60332-2-2:2005) Tests on electric and optical fibre cables under fire conditions - Part 2-2: Test for vertical flame propagation for a single small insulated wire or cable - Procedure for diffusion flame |
| EN IEC 60332-3-24 | EN IEC 60332-3-24:2018 (OVE EN IEC 60332-3-24:2019) Tests on electric and optical fibre cables under fire conditions - Part 3-24: Test for vertical flame spread of vertically-mounted bunched wires or cables - Category C |
| EN 60754-1 | EN 60754-1:2014 + A1:2020 (OVE EN 60754-1:2021) Test on gases evolved during combustion of materials from cables – Part 1: Determination of the halogen acid gas content |
| EN ISO 9223 | EN ISO 9223:2012 (ÖNORM EN ISO 9223:2012) Korrosion von Metallen und Legierungen - Korrosivität von Atmosphären - Klassifizierung, Bestimmung und Abschätzung |
| EN 60068-2-64 | EN 60068-2-64:2008 + A1:2019 (OVE EN 60068-2-64:2020) Environmental testing - Part 2-64: Tests - Test Fh: Vibration, broadband random and guidance |
| EN IEC 62443-4-2 | EN IEC 62443-4-2:2019 + AC:2022 (OVE EN IEC 62443-4-2:2020) Security for industrial automation and control systems – Part 4-2: Technical security requirements for IACS components |
| OEBB R10 | ÖBB Merkheft R10, Stand 01.01.2022 Eisenbahnanlagen: Schwerpunktkonzept aus Sicht des Arbeitnehmer/innenschutzes |
| WEEE | WEEE Directive 2012/19/EU Directive 2012/19/EU of the European Parliament and of the Council of 4 July 2012 on waste electrical and electronic equipment |
| RoHS | Directive 2011/65/EU of the European Parliament and of the Council of 8 June 2011 on the restriction of the use of certain hazardous substances in electrical and electronic equipment (recast). Consolidated version of 24 June 2015. |
| REACH | Regulation (EC) No 1907/2006 - REACH of 18 December 2006 concerning the Registration, Evaluation, Authorisation and Restriction of Chemicals (REACH) and establishing a European Chemicals Agency |

# Issues, decisions and justifications

Sorted list of all references to module IDJ in this document.

This chapter describes clarifications concerning the overall system SSS, therefore not all specifications are listed here. Additionally, based on the appropriate input of the PLM (usually by email) the decision for the technical project how to proceed is documented here.

| GENCAB:HW-SSS:IDJ:ID:0001 |  | Space demand |  | (Accepted) |
| --- | --- | --- | --- | --- |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Issue: |  |  |  |  |
|  | From: HOLZKNECHT Robert <robert.holzknecht@urbanandmainlines.com> Sent: Mittwoch, 13. Dezember 2023 13:35 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Cc: BAUMGARTNER Dieter <dieter.baumgartner@urbanandmainlines.com>; GOLDENITS Mario <mario.goldenits@urbanandmainlines.com> Subject: AW: [BFZ-3.x:SRS:REQ:0193] — Georedundanz - Platzbedarf - Server und Network RACKs Classified as: {OPEN} Hallo Bernhard, dass der Schrank, entgegen meinen bzw. der zuletzt vom Kunden bestätigten Dimensionen nun um 9,4cm größer ist und zusammen mit der Information dass dies für Transport/Montage kein Problem darstellt , als auch im Raum genug Platz vorhanden ist, ist die Änderung tolerierbar. Lg Robert [@@ THALES GROUP LIMITED DISTRIBUTION @@] Von: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Gesendet: Mittwoch, 13. Dezember 2023 13:25 An: HOLZKNECHT Robert <robert.holzknecht@urbanandmainlines.com> Cc: BAUMGARTNER Dieter <dieter.baumgartner@urbanandmainlines.com>; GOLDENITS Mario <mario.goldenits@urbanandmainlines.com> Betreff: [BFZ-3.x:SRS:REQ:0193] — Georedundanz - Platzbedarf - Server und Network RACKs Classified as: {OPEN} Hallo Robert, In dem genannten Requirement wird eine vom Kunden bestätigte Größe des generischen Schrankes gefordert. Die Abmessungen eines Schranks dürfen dabei 800 mm x 1200 mm x 2006 mm nicht überschreiten. Wir sind im Laufe der Enticklung auf einen RITTAL-Schrank umgestiegen. Dieser ist aktuell mit Sockel ausgeführt und weicht in der Höhe ab. Die Sockelhöhe beträgt 100mm, somit weist der Schrank eine Gesamthöhe von 2100mm auf. Der Sockel ist einfach abnehmar beim Transport und sollte daher kein Problem darstellen. Die Raumhöhe vor Ort ist auch absolut ausreichend. Kannst du bitte bestätigen, dass der Schrank mit Sockel mit den Dimensionen 800 mm x 1200 mm x 2100 mm so verwendet werden kann? Danke LG Bernhard |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Decision: |  |  |  |  |
|  | The customer accepted the usage of a larger cabinet. (800mm x 1200mm x 2006 mm; WxDxH). Product Management and Technics department confirmed the actual size of 800mm x 1200mm x 2100mm including socket. |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Requirements in HW-SSS: |  |  |  |  |
|  | [GENCAB:HW-SSS:REQ:0012] Space demand [GENCAB:HW-SSS:REQ:0100] Packaging |  |  |  |
| Requirements in Overall System SSS: |  |  |  |  |
|  | [BFZ-2.x:SRS:REQ:0178] HW Platzbedarf Rechnerraum |  |  |  |

| GENCAB:HW-SSS:IDJ:ID:0002 |  | Uniform Branding |  | (Accepted) |
| --- | --- | --- | --- | --- |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Issue: |  |  |  |  |
|  | From: HOLZKNECHT Robert Sent: Donnerstag, 22. Dezember 2022 10:36 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Cc: BAUMGARTNER Dieter <dieter.baumgartner@urbanandmainlines.com> Subject: AW: OMC 3.0 Uniform branding [BFZ-2.x:SRS:REQ:0208], [BFZ:FL:FEA:0120] Hallo Bernhard, hiermit bestätige ich, dass es keine speziellen Anforderungen bezüglich Branding der Schränke von Seiten der ÖBB gibt. Lg, Robert [@@ THALES GROUP LIMITED DISTRIBUTION @@] Von: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Gesendet: Donnerstag, 22. Dezember 2022 08:33 An: HOLZKNECHT Robert <robert.holzknecht@urbanandmainlines.com> Cc: BAUMGARTNER Dieter <dieter.baumgartner@urbanandmainlines.com> Betreff: OMC 3.0 Uniform branding [BFZ-2.x:SRS:REQ:0208], [BFZ:FL:FEA:0120] Hallo Robert, Kannst du bestätigen, dass es keine speziellen Anforderung des Kunden an die Schränke bezüglich GTS Branding gibt? Danke LG Bernhard |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Decision: |  |  |  |  |
|  | There are no specific customer requirements regarding branding. |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Requirements in HW-SSS: |  |  |  |  |
|  | [GENCAB:HW-SSS:REQ:0014] Uniform branding |  |  |  |
| Requirements in Overall System SSS: |  |  |  |  |
|  | [BFZ-2.x:SRS:REQ:0208] Einheitliches Branding |  |  |  |

| GENCAB:HW-SSS:IDJ:ID:0003 |  | Cabinet components |  | (Accepted) |
| --- | --- | --- | --- | --- |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Issue: |  |  |  |  |
|  | From: GRUENSTEIDL Guenter <guenter.gruensteidl@urbanandmainlines.com> Sent: Montag, 3. Juli 2023 07:58 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com>; MESSNER Robert - Contractor <robert.messner-ext@urbanandmainlines.com> Subject: RE: OMC 3.0 Konfiguration HW Generischer Serverschrank/Netzwerkschrank Hallo Bernhard, ist für BFZ 3.x o.k.. LG Günter From: MESSNER Robert - Contractor <robert.messner-ext@urbanandmainlines.com> Sent: Freitag, 30. Juni 2023 13:30 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com>; GRUENSTEIDL Guenter <guenter.gruensteidl@urbanandmainlines.com> Subject: Re: OMC 3.0 Konfiguration HW Generischer Serverschrank/Netzwerkschrank Im meiner Rolle als PDA kann ich dir bestätigen dass diese Bestückung ausreicht für die EL4. Leider deck es sich aktuell nicht mit der Ausschreibung, aber wir werden alles tun damit wir den generischen Serverschrank und generischen Netwerkschrank in der EL4 verwenden können. Vermutlich in einer Minderbestückung. LG From: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Sent: Freitag, 30. Juni 2023 12:40 To: GRUENSTEIDL Guenter <guenter.gruensteidl@urbanandmainlines.com>; MESSNER Robert - Contractor <robert.messner-ext@urbanandmainlines.com> Subject: OMC 3.0 Konfiguration HW Generischer Serverschrank/Netzwerkschrank Hallo, Könnt ihr mir bestätigen, dass die generische Konfiguration für den Server- und den Netzwerkschrank wie unten angeführt ausreichend dimensioniert ist für die Projekte BFZ 3.x und ELEKTRA 4.0? Generischer Serverschrank - 4 x Switches (2 Switches für BFZ 3.0) - 15 x Server (1 x Control plane, 11 x Computing Server, 3 x Storage Server) - RAM: 12x64GB - CPU: AMD, 3,25GHz 32 Core (64 Threads), 2x960GB SATA SFF (Control plane und computing Server, 8x960GB für Storage Server) - 2x2 Ethernet Ports (1x2 Ports für BFZ 3.0) - 1 x KVM - 2 x PDU Generischer Netzwerkschrank - 2 x Router - 10 x Switches (4 Switches für BFZ 3.0) - 2 x PDU Danke LG Bernhard |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Decision: |  |  |  |  |
|  | The configuration of the HW is sufficient to meet the performance requirements also for OMC 3.x and ELEKTRA 4.0. |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Requirements in HW-SSS: |  |  |  |  |
|  | [GENCAB:HW-SSS:REQ:0001] Network cabinet - HW components [GENCAB:HW-SSS:REQ:0005] Network cabinet components [GENCAB:HW-SSS:REQ:0006] Server cabinet components [GENCAB:HW-SSS:REQ:0002] Server cabinet - HW components [GENCAB:HW-SSS:REQ:0090] Switch server cabinet - High availability of CNs [GENCAB:HW-SSS:REQ:0115] Cabinet - Connection to routers of the network cabinet II |  |  |  |
| Requirements in Overall System SSS: |  |  |  |  |
|  | [BFZ-2.x:SRS:REQ:0166] Anzahl USt und Weichen [BFZ-3.x:SRS:REQ:0023] Georedundanz - Wiederverwendbarkeit für andere Produkte [BFZ-3.x:SRS:REQ:0189] Georedundanz - Anzahl der Standorte [BFZ-3.x:SRS:REQ:0187] Georedundanz - Maximale Anzahl der EBO2 OMC Arbeitsplätze |  |  |  |

| GENCAB:HW-SSS:IDJ:ID:0006 |  | Manual corrective maintenance - MRT 1h |  | (Accepted) |
| --- | --- | --- | --- | --- |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Issue: |  |  |  |  |
|  | From: SCHEUER Markus <markus.scheuer@urbanandmainlines.com> Sent: Freitag, 9. Februar 2024 17:01 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Cc: MOSER Florian <florian.moser@urbanandmainlines.com> Subject: Verfeinerung und Korrektur von GENCAB:HW-SSS:REQ:0078 - MDR Hier als Verfeinerung und Korrektur von GENCAB:HW-SSS:IDJ:ID:0006: Entsprechend der Review-Kommentare der HW-SSS ist eine Unterteilung der MRT in HW-nahe und SW-nahe Aktivitäten sinnvoll. Diese sieht wie folgt aus: Es wird eine MRT von 1 Stunde angenommen. Es werden ¾ dieser MRT für HW-bezogene Aktivitäten bis zum erfolgreichen Einschalten angenommen und ¼ der MRT für weitere SW-spezifische Aktivitäten. lG. Markus From: SCHEUER Markus <markus.scheuer@urbanandmainlines.com> Sent: Dienstag, 27. Juni 2023 09:52 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Cc: MOSER Florian <florian.moser@urbanandmainlines.com> Subject: RE: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0087] bzw. [BFZ-3.x:SRS:REQ:0197] & [BFZ-3.x:SRS:REQ:0198] Hallo Bernhard, Ja, das kann ich bestätigen. Vielen Dank, lG. Markus From: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Sent: Dienstag, 27. Juni 2023 07:28 To: SCHEUER Markus <markus.scheuer@urbanandmainlines.com> Subject: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0087] bzw. [BFZ-3.x:SRS:REQ:0197] & [BFZ-3.x:SRS:REQ:0198] Hallo Markus, Kannst du bestätigen, dass aufgrund der hohen Verfügbarkeitsanforderungen für das BFZ Gesamtsystem (und auch Subsystem) eine MTTR von einer Stunde für die Hardware eines einzelnen Schrankes (Serverschrank und Netzwerkschrank) folgt? Danke LG Bernhard |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Decision: |  |  |  |  |
|  | Due to high availability requirements for the OMC System, a MRT of 1h follows, ¾h for HW activities plus ¼h for SW activties. |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Requirements in HW-SSS: |  |  |  |  |
|  | [GENCAB:HW-SSS:REQ:0087] Manual corrective maintenance - MRT 1 h |  |  |  |
| Requirements in Overall System SSS: |  |  |  |  |

| GENCAB:HW-SSS:IDJ:ID:0007 |  | Cabinet equipment practice - Doors |  | (Accepted) |
| --- | --- | --- | --- | --- |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Issue: |  |  |  |  |
|  | From: HOLZKNECHT Robert <robert.holzknecht@urbanandmainlines.com> Sent: Montag, 26. Juni 2023 12:07 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Subject: AW: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0107] bzw. [BFZ-3.x:SRS:REQ:0023] Georedundanz - Wiederverwendbarkeit für andere Produkte Hallo Bernhard, zumindest von meiner Seite aus gibt es keine solche Forderung. Die Zugänglichkeit und Wartbarkeit soll natürlich optimal umgesetzt werden. Wenn Doppeltüren dazu die Lösung sind, werde ich dem nicht widersprechen. Lg, Robert [@@ THALES GROUP LIMITED DISTRIBUTION @@] Von: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Gesendet: Montag, 26. Juni 2023 09:22 An: HOLZKNECHT Robert <robert.holzknecht@urbanandmainlines.com> Betreff: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0107] bzw. [BFZ-3.x:SRS:REQ:0023] Georedundanz - Wiederverwendbarkeit für andere Produkte Hallo Robert, Kannst du bestätigen, dass für die bessere Zugänglichkeit und bessere Wartbarkeit an der Vorder- und Rückseite des generischen Server- und Netzwerkschranks geteilte Türen verbaut werden sollen? Danke LG Bernhard |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Decision: |  |  |  |  |
|  | The cabinets shall be equiped with divided doors. |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Requirements in HW-SSS: |  |  |  |  |
|  | [GENCAB:HW-SSS:REQ:0107] Cabinet equipment practice - Doors |  |  |  |
| Requirements in Overall System SSS: |  |  |  |  |
|  | [BFZ-3.x:SRS:REQ:0023] Georedundanz - Wiederverwendbarkeit für andere Produkte |  |  |  |

| GENCAB:HW-SSS:IDJ:ID:0008 |  | Cabinet equipment practice - Power supply cable entry |  | (Accepted) |
| --- | --- | --- | --- | --- |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Issue: |  |  |  |  |
|  | From: HOLZKNECHT Robert <robert.holzknecht@urbanandmainlines.com> Sent: Montag, 26. Juni 2023 09:37 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Subject: AW: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0108] bzw. [BFZ-3.x:SRS:REQ:0023] Georedundanz - Wiederverwendbarkeit für andere Produkte Hallo Bernahrd, kann ich bestätigen. Lg, Robert [@@ THALES GROUP LIMITED DISTRIBUTION @@] Von: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Gesendet: Montag, 26. Juni 2023 09:23 An: HOLZKNECHT Robert <robert.holzknecht@urbanandmainlines.com> Betreff: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0108] bzw. [BFZ-3.x:SRS:REQ:0023] Georedundanz - Wiederverwendbarkeit für andere Produkte Hallo Robert, Kannst du bitte bestätigen, dass aufgrund der Stromversorgung am Einsatzstandort des generischen Server- und Netzwerkschrankes, die Verkabelung der Stromversorgung von oben erfolgen muss? Danke LG Bernhard |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Decision: |  |  |  |  |
|  | Power supply connection shall be supported from the top. |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Requirements in HW-SSS: |  |  |  |  |
|  | [GENCAB:HW-SSS:REQ:0108] Cabinet equipment practice - Power supply cable entry |  |  |  |
| Requirements in Overall System SSS: |  |  |  |  |
|  | [BFZ-3.x:SRS:REQ:0023] Georedundanz - Wiederverwendbarkeit für andere Produkte |  |  |  |

| GENCAB:HW-SSS:IDJ:ID:0009 |  | Cabinet equipment practice - Cable entry for external connection |  | (Accepted) |
| --- | --- | --- | --- | --- |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Issue: |  |  |  |  |
|  | From: HOLZKNECHT Robert <robert.holzknecht@urbanandmainlines.com> Sent: Montag, 26. Juni 2023 12:04 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Subject: AW: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0109] bzw. [BFZ-3.x:SRS:REQ:0023] Georedundanz - Wiederverwendbarkeit für andere Produkte Hallo Bernhard, Die offizielle Vorgabe ist, dass wir die Verkabelung von oben machen. Wenn es jedoch mit wenig Aufwand machbar ist hier flexibler zu sein (z. B. weil es eben nur ein Blech braucht), dann ist das für mich okay. Wichtig ist, dass die Aufwände nicht ausufern und sich so gut wie neutral verhalten. Lg, Robert [@@ THALES GROUP LIMITED DISTRIBUTION @@] Von: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Gesendet: Montag, 26. Juni 2023 09:24 An: HOLZKNECHT Robert <robert.holzknecht@urbanandmainlines.com> Betreff: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0109] bzw. [BFZ-3.x:SRS:REQ:0023] Georedundanz - Wiederverwendbarkeit für andere Produkte Hallo Robert, Kannst du bitte bestätigen, dass aufgrund eines Kundenwunsches, der generische Server- und Netzwerkschrank externe Verbindungen von oben und unten ermöglichen muss? Danke LG Bernhard |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Decision: |  |  |  |  |
|  | External connections shall be supported from top and bottom. |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Requirements in HW-SSS: |  |  |  |  |
|  | [GENCAB:HW-SSS:REQ:0109] Cabinet equipment practice - Cable entry for external connection |  |  |  |
| Requirements in Overall System SSS: |  |  |  |  |
|  | [BFZ-3.x:SRS:REQ:0023] Georedundanz - Wiederverwendbarkeit für andere Produkte |  |  |  |

| GENCAB:HW-SSS:IDJ:ID:0010 |  | Availability - Internal network |  | (Accepted) |
| --- | --- | --- | --- | --- |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Issue: |  |  |  |  |
|  | From: SCHEUER Markus <markus.scheuer@urbanandmainlines.com> Sent: Montag, 26. Juni 2023 13:54 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Cc: MOSER Florian <florian.moser@urbanandmainlines.com> Subject: RE: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0024] bzw. [BFZ-3.x:SRS:REQ:0197] & [BFZ-3.x:SRS:REQ:0198] Hallo Bernhard, Ja, das kann ich bestätigen. Es mag auf den ersten Blick seltsam erscheinen, dass für das BFZ-Subsystem eine höhere Verfügbarkeit gefordert ist, als für den generischen Netzwerkschrank, der ja auch ein Teil des BFZ-Subsystems darstellt (und somit eine höhere Verfügbarkeit haben müsste als das ganze Subsystem). Beim passiven BFZ-Subsystem wird aber nur ein Anteil der tatsächlich berechneten Verfügbarkeit schlagend (keine betriebliche Auswirkung und nur ein kleiner Anteil, der nicht fail-silent ist). lG. Markus From: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Sent: Montag, 26. Juni 2023 09:24 To: SCHEUER Markus <markus.scheuer@urbanandmainlines.com> Subject: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0024] bzw. [BFZ-3.x:SRS:REQ:0197] & [BFZ-3.x:SRS:REQ:0198] Hallo Markus, Kannst du bitte bestätigen, dass aufgrund der Verfügbarkeitsanforderungen von 99,99995% für das passive BFZ-Subsystem und aus den Verfügbarkeitsanforderungen für das BFZ-Gesamtsystem ([BFZ-3.x:SRS:REQ:0197] & [BFZ-3.x:SRS:REQ:0198]), eine Verfügbarkeit von 99,9999% für den einzelnen generischen Netzwerkschrank folgt? Danke LG Bernhard |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Decision: |  |  |  |  |
|  | Availability of 99,9999% for one generic network cabinet is required. |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Requirements in HW-SSS: |  |  |  |  |
|  | [GENCAB:HW-SSS:REQ:0024] Availability - Internal network |  |  |  |
| Requirements in Overall System SSS: |  |  |  |  |

| GENCAB:HW-SSS:IDJ:ID:0011 |  | Single failure - Diagnosis |  | (Accepted) |
| --- | --- | --- | --- | --- |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Issue: |  |  |  |  |
|  | From: SCHEUER Markus <markus.scheuer@urbanandmainlines.com> Sent: Montag, 26. Juni 2023 13:57 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Cc: MOSER Florian <florian.moser@urbanandmainlines.com> Subject: RE: RE: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0081] bzw. [BFZ-3.x:SRS:REQ:0194] Hallo Bernhard, Ja, das kann ich. Es ist zusätzlich auch davon auszugehen, dass stärkere Diagnoseanforderung als bei der BFZ 2.x diese Eigenschaft benötigen. lG. Markus From: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Sent: Montag, 26. Juni 2023 13:06 To: SCHEUER Markus <markus.scheuer@urbanandmainlines.com> Subject: RE: OMC 3.0 Anforderung [GENCAB:HW-SSS:REQ:0081] bzw. [BFZ-3.x:SRS:REQ:0194] Hallo Markus, Kannst du bestätigen, dass für ein Erreichen der hohen Verfügbarkeitsanforderungen and das BFZ-System und BFZ Subsystem ein Diagnosesystem für Einzelfehler von LRUs notwendig ist, um im Fehlerfall so schnell wie möglich die Einzelkomponenten tauschen zu können? Danke LG Bernhard |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Decision: |  |  |  |  |
|  | Diagnosis system for failure detection of LRUs necessary. |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Requirements in HW-SSS: |  |  |  |  |
|  | [GENCAB:HW-SSS:REQ:0081] Single Failure - Diagnosis |  |  |  |
| Requirements in Overall System SSS: |  |  |  |  |
|  | [BFZ-3.x:SRS:REQ:0194] Keine betriebliche Auswirkung bei einem Einfachfehler im BFZ-System |  |  |  |

| GENCAB:HW-SSS:IDJ:ID:0012 |  | Sensor for environmental parameters |  | (Accepted) |
| --- | --- | --- | --- | --- |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Issue: |  |  |  |  |
|  | From: HOLZKNECHT Robert <robert.holzknecht@urbanandmainlines.com> Sent: Donnerstag, 29. Juni 2023 11:58 To: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Cc: BAUMGARTNER Dieter <dieter.baumgartner@urbanandmainlines.com> Subject: AW: OMC 3.0 Temperatur- Feuchtesensor Hallo Bernhard, ist hiermit bestätigt. Lg, Robert [@@ THALES GROUP LIMITED DISTRIBUTION @@] Von: MANDL Bernhard - Contractor <bernhard.mandl-ext@urbanandmainlines.com> Gesendet: Donnerstag, 29. Juni 2023 07:37 An: HOLZKNECHT Robert <robert.holzknecht@urbanandmainlines.com> Cc: BAUMGARTNER Dieter <dieter.baumgartner@urbanandmainlines.com> Betreff: OMC 3.0 Temperatur- Feuchtesensor Hallo Robert, Kannst du bitte bestätigen, dass wir für den generischen Serverschrank einen Temperatur- und Feuchtesensor verwenden müssen? Vielen Dank LG Bernhard |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Decision: |  |  |  |  |
|  | Temperature and humidity sensor must be assembled. |  |  |  |
| --------------------------------------------------------------------------------------------------------------------------------------------------------------- Requirements in HW-SSS: |  |  |  |  |
|  | [GENCAB:HW-SSS:REQ:0116] Sensor for environmental parameters |  |  |  |
| Requirements in Overall System SSS: |  |  |  |  |

Furthermore, this chapter describes the architectural decisions taken at the overall [DIL] system level.

| EL4:IDJ-RA:ID:0037 |  | Split-brain avoidance |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Decision: | IPS, ADM and VIL shall create solution that is aligned with the proposal described in the "Split-brain avoidance" technical concept document. |  |  |  |  |
| Status: | In negotiation |  |  | Priority: | Medium |
| Decision Date: |  |  |  | Decision Authority: | Architectural Expert team from VIL and IPS. |
| Requirements: | EL4-IPS-SSS-REQ-00058, EL4-IPS-SSS-REQ-00061, EL4-IPS-SSS-REQ-00062, EL4-IPS-SSS-REQ-00059, EL4-IPS-SSS-REQ-00060, EL4-IPS-SSS-REQ-00063, EL4-IPS-SSS-REQ-00064, GENCAB:HW-SSS:REQ:0140, GENCAB:HW-SSS:REQ:0141 |  |  |  |  |
| Analysis: | Customer expects that DIL-CU will be available and operate safely in case of geo-site outage, availability zone (rack) outage and various double faults [TBD ref to the system level requiremets with the list of faults DIL shall operate]. Availability of DIL-CU and VILs are defined in customer's requirements [D2.2_Teillastenheft_RAMS_V1.3]. To meet these safety and availability criteria in case of outages and multiple faults [ref to the req], technical concept for the "Split-brain avoidance" was developed and is described in [3BU_15000_6851_DSAPA]. The document also contains analysis of foreseeable failure scenarios with double (and more) faults wrt. safety and availability. |  |  |  |  |

# Requirements

## General Requirements

| [GENCAB:HW-SSS:REQ:0001] — GCR |  | Network cabinet - HW components |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The equipment of the generic network cabinet shall be scalable, applicable for other products and shall support the geo-redundancy concept. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0023]: Georedundanz - Wiederverwendbarkeit für andere Produkte [BFZ-3.x:SRS:REQ:0366]: Georedundanz - BFZ System [GENCAB:HW-SSS:IDJ:ID:0003]: Cabinet components |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Network cabinet |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Qualification of maximum possible assembly shall be done. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0002] — GCR |  | Server cabinet - HW components |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The equipment of the generic server cabinet shall be scalable, applicable for other products and shall support the geo-redundancy concept. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0023]: Georedundanz - Wiederverwendbarkeit für andere Produkte [BFZ-3.x:SRS:REQ:0366]: Georedundanz - BFZ System [GENCAB:HW-SSS:IDJ:ID:0003]: Cabinet components |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Server cabinet |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Qualification of maximum possible assembly shall be done. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0139] — GCR |  | Server distribution |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The (re-)placement of the servers of the same type across the availability zones shall follow the balanced distribution principle. Server types are control server, compute server and storage server |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-01483]: Server distribution [EL4-SSS-REQ-01484]: Server reintegration |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Server cabinet |
| Verification Method: | Inspection/Review Analysis |  |  | Verification Step: | review analysis |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

## Operational Requirements

| [GENCAB:HW-SSS:REQ:0010] — MDR |  | Maintenance intervall |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The HW components shall be maintenance-free. If this cannot be achieved, a minimum maintenance interval of 6 months shall be allowed. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0404]: Wartung und Instandsetzung [EL4-SSS-REQ-00359]: Maintainability and Maintenance - No Inspection and Maintenance [EL4-SSS-REQ-00360]: Maintainability and Maintenance - No preventive Maintenance |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-2.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | On-site maintenance is limited to maintenance of hardware components. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0106] — MDR |  | Maintenance - Design |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Servers and cables shall be easily accessible for maintenance. Therefore, the servers shall be able to be pulled out fully during operation and cable management shall be done with cable management arms. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0404]: Wartung und Instandsetzung [EL4-SSS-REQ-00361]: Maintainability and Maintenance - Easy Accessibilty |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Technics (R&D) |  |  | Cabinet: | Server cabinet |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | To ensure a simple and pleasant server maintenance. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0008] — GCR |  | Product lifecycle |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The HW equipment shall be selected with COTS components and standard techniques to support a useful life of at least 25 years. |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0205]: Produkt Nutzungsdauer |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-2.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | E.g. components with long lifetime, clearly defined interfaces for exchange of discontinued components, etc. (Necessary to fulfil demanding dependability and maintenance requirements.) |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0145] — GCR |  | Minimum Useful Life - COTS Components |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The minimum useful life of the (COTS) components shall be at least 7 years (24 hours, 7 days a week). |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00299]: Minimum Useful Life - Indoor System - COTS Components |  |  |  |  |
| Status: | in negotiation |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Analysis |  |  | Verification Step: | analysis |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0146] — GCR |  | Minimum supply period - spare parts |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The minimum spare parts supply period to maintain operation and full functionality of components shall be at least 7 years. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00302]: Supply for Spare Parts |  |  |  |  |
| Status: | in negotiation |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Analysis |  |  | Verification Step: | analysis |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0009] — GCR |  | Product lifecycle - Upwards compatibility and obsolescence handling |  |  |  |
| --- | --- | --- | --- | --- | --- |
| To ensure upwards compatibility for further developments and a minimum necessary effort regarding adaption, testing, integration and approval in case of equipment obsolescence within the useful lifetime of the hardware, COTS components and 19" technology for the HW components shall be used. |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0205]: Produkt Nutzungsdauer [BFZ-3.x:SRS:REQ:0030]: Geo-redundancy - HW Obsoleszenz [BFZ-3.x:SRS:REQ:0353]: COTS Clusterlösungen für nicht-sicherheitsbezogene Funktionen [BFZ-3.x:SRS:REQ:0354]: COTS Clusterlösungen für sicherheitsbezogene Funktionen |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-2.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0027] — DOR |  | Installation manual |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A generic installation manual for the HW shall be provided. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0337]: Georedundanz - Roll-out - Tools und unterstützende Dokumentation [EL4-SSS-REQ-00345]: Maintainability and Maintenance - Documentation - Usability [EL4-SSS-REQ-00346]: Maintainability and Maintenance - Documentation - Generic Form [EL4-SSS-REQ-00347]: Maintainability and Maintenance - Documentation - Electronic Form [EL4-SSS-REQ-00348]: Maintainability and Maintenance - Documentation - File Format |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0028] — DOR |  | Maintenance manual |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A generic maintenance manual for the HW shall be provided. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0337]: Georedundanz - Roll-out - Tools und unterstützende Dokumentation [BFZ-3.x:SRS:REQ:0005]: Georedundanz - Wiederinbetriebnahme - Dokumentation und Schulung [EL4-SSS-REQ-00345]: Maintainability and Maintenance - Documentation - Usability [EL4-SSS-REQ-00346]: Maintainability and Maintenance - Documentation - Generic Form [EL4-SSS-REQ-00347]: Maintainability and Maintenance - Documentation - Electronic Form [EL4-SSS-REQ-00348]: Maintainability and Maintenance - Documentation - File Format |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | The maintenance manual will also contain HW relevant steps to put everything in operation after a complete outage / shutdown. This manual also provides a complete HW description. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0086] — MDR |  | Maintenance impact on System availability |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A corrective/or planned maintenance activity and/or replacement of failed/defective LRU shall not affect the operational availability of other LRUs and shall have no adverse effect on the operation and reliability of the system as a whole. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0195]: Verfügbarkeit eines BFZ-Systems gesamt (Klasse 1) [BFZ-3.x:SRS:REQ:0196]: Verfügbarkeit eines aktiven BFZ-Subsystems gesamt (Klasse 1) [BFZ-3.x:SRS:REQ:0197]: Verfügbarkeit eines passiven BFZ-Subsystems gesamt (Klasse 1) [BFZ-3.x:SRS:REQ:0198]: Aufteilung Verfügbarkeit BFZ-System gesamt [BFZ-3.x:SRS:REQ:0199]: Aufteilung Verfügbarkeit aktives BFZ-Subsystem gesamt [BFZ-3.x:SRS:REQ:0200]: Aufteilung Verfügbarkeit passives BFZ-Subsystem gesamt [EL4-SSS-REQ-00322]: Reliability - Replacement of HW Component - No operational Impact [EL4-SSS-REQ-00692]: Safety - Maintenance - Activities [EL4-SSS-REQ-00313]: Availability - LRU - No Maintenance Impact |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0087] — MDR |  | Manual corrective maintenance - MRT 1 h |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The manual corrective maintenance actions of a HW component (incl. router, switches, control plane, computing server, storage engine) like exchange, cabling, etc. up to the successful power-on shall be done within 45 minutes of an MRT = 1 hour. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0195]: Verfügbarkeit eines BFZ-Systems gesamt (Klasse 1) [BFZ-3.x:SRS:REQ:0196]: Verfügbarkeit eines aktiven BFZ-Subsystems gesamt (Klasse 1) [BFZ-3.x:SRS:REQ:0197]: Verfügbarkeit eines passiven BFZ-Subsystems gesamt (Klasse 1) [BFZ-3.x:SRS:REQ:0198]: Aufteilung Verfügbarkeit BFZ-System gesamt [BFZ-3.x:SRS:REQ:0199]: Aufteilung Verfügbarkeit aktives BFZ-Subsystem gesamt [BFZ-3.x:SRS:REQ:0200]: Aufteilung Verfügbarkeit passives BFZ-Subsystem gesamt [EL4-SSS-REQ-00357]: Maintainability and Maintenance - Component Replacement - Manual corrective Maintenance Actions [GENCAB:HW-SSS:IDJ:ID:0006]: Manual corrective maintenance - MRT 1h |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | We expect the maintenance stuff with the HW component is ready for the maintenance action. Roughly ¾ of the MRT (Mean repair time) is needed for exchange of the material, necessary cabling and power-on of the component to check that it is ready for SW-updates. The other time, which is expected to be ¼ of the MRT can be used for SW-update and integration until the component is ready for operation. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0121] — FUR |  | Automatic Start-up of HW components |  |  |  |
| --- | --- | --- | --- | --- | --- |
| After automatic server shutdowns or when the power supply is restored after supply [failure]s, all HW components shall return to the state they were in before the failure. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00655]: Startup VIL Node - No Configuration Change - Automatic Start-up |  |  |  |  |
| Status: | to be descoped |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | system test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0122] — DPR |  | Minimum Useful Life - Continuous Utilisation |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The supplier shall guarantee the continuous utilisation of the system within the minimum useful life of 7 years (24h a day, 7 day a week). |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00300]: Minimum Useful Life - Continuous Utilisation |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Analysis |  |  | Verification Step: | analysis |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0124] — MDR |  | Maintainability and Maintenance - Component Replacement - Approved Tools |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Only the following tools may be used for each replaceable component: - Phillips screwdriver - Slotted screwdriver - Socket wrench - Hex wrench - Torx wrench - Open-end wrench |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00355]: Maintainability and Maintenance - Component Replacement - Approved Tools [EL4-SSS-REQ-00356]: Maintainability and Maintenance - Component Replacement - Standard Tools |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0134] — MDR |  | Maintainability and Maintenance - Spare Parts Storage - Concept |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A storage concept for the spare parts as described in the service description shall be developed and provided. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00334]: Maintainability and Maintenance - Spare Parts Storage - Concept |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | == MISMATCH == This is a requirement, but in the LH it is only marked as "Info The requirement must be specified in detail. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0135] — MDR |  | Maintainability and Maintenance - Spare Parts Storage - Information |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The necessary information and facilities for spare parts storage shall be provided. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00335]: Maintainability and Maintenance - Spare Parts Storage - Information |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | review |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | The requirement must be specified in detail. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0136] — MDR |  | Maintainability and Maintenance - Spare Parts Storage - Effort |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Components shall be developed in such a way that storage is possible with no special measures. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00336]: Maintainability and Maintenance - Spare Parts Storage - Effort |  |  |  |  |
| Status: | to be descoped |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | == OPEN POINT == Requirement has to be refined according to EN50125-3 or EN 60721-3. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0137] — MDR |  | Maintainability and Maintenance - Spare Parts Storage - Maintenance |  |  |  |
| --- | --- | --- | --- | --- | --- |
| All spare parts shall be storable without requiring regular maintenance and without being kept under voltage. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00337]: Maintainability and Maintenance - Spare Parts Storage - Maintenance |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Exceptions for individual components require an alternative solution from the contractor and shall be approved by the customer. |  |  |  |  |

## Physical Requirements

| [GENCAB:HW-SSS:REQ:0003] — GCR |  | Network cabinet equipment practice |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The network cabinet shall provide a 19" shelfs for the components. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0023]: Georedundanz - Wiederverwendbarkeit für andere Produkte |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Technics (R&D) |  |  | Cabinet: | Network cabinet |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | A 19” shelf is standard technology for COTS components and therefore necessary for product lifecycle. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0004] — GCR |  | Server cabinet equipment practice |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The server cabinet shall provide a 19" shelf for the components. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0023]: Georedundanz - Wiederverwendbarkeit für andere Produkte |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Technics (R&D) |  |  | Cabinet: | Server cabinet |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | A 19” shelf is standard technology for COTS components and therefore necessary for product lifecycle. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0012] — PER |  | Space demand |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The HW space demand of one cabinet shall not exceed 800mm x 1200mm x 2100mm (WxDxH) per cabinet. |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0178]: HW Platzbedarf Rechnerraum [BFZ-3.x:SRS:REQ:0193]: Georedundanz - Platzbedarf - Server und Network RACKs [EL4-SSS-REQ-01091]: Data Center Location - Space for Doors and Aisles [GENCAB:HW-SSS:IDJ:ID:0001]: Space demand |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Technics (R&D) |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Larger cabinet size is confirmed by customer. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0144] — PER |  | Double doors |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Double doors at the front and rear shall each be 400 mm wide. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-01091]: Data Center Location - Space for Doors and Aisles |  |  |  |  |
| Status: | in negotiation |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Technics (R&D) |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Larger cabinet size is confirmed by customer. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0100] — PER |  | Packaging |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Suitable packaging complying with [EN 60721-3-2] for a cabinet size of up to 800mm x 1200mm x 2100mm (WxDxH) for transport shall be defined in accordance with the [ELEKTRA Environmental Conditions] Chapter 3.2.3 |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0178]: HW Platzbedarf Rechnerraum [BFZ-3.x:SRS:REQ:0193]: Georedundanz - Platzbedarf - Server und Network RACKs [GENCAB:HW-SSS:IDJ:ID:0001]: Space demand |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Technics (R&D) |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0107] — PER |  | Cabinet equipment practice - Doors |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The cabinet shall be equipped with perforated and divided doors on front and back side. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0023]: Georedundanz - Wiederverwendbarkeit für andere Produkte [EL4-SSS-REQ-01091]: Data Center Location - Space for Doors and Aisles [EL4-SSS-REQ-01119]: Cooling Concept - Topics [EL4-SSS-REQ-01122]: Cooling Concept - Air Flow [GENCAB:HW-SSS:IDJ:ID:0007]: Cabinet equipment practice - Doors |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Technics (R&D) |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0108] — PER |  | Cabinet equipment practice - Power supply cable entry |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The cabinet shall support UPS cable entry from the top. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0023]: Georedundanz - Wiederverwendbarkeit für andere Produkte [GENCAB:HW-SSS:IDJ:ID:0008]: Cabinet equipment practice - Power supply cable entry |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Technics (R&D) |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0109] — PER |  | Cabinet equipment practice - Cable entry for external connection |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The cabinet shall support cable entry for external connection from top and bottom. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0023]: Georedundanz - Wiederverwendbarkeit für andere Produkte [GENCAB:HW-SSS:IDJ:ID:0009]: Cabinet equipment practice - Cable entry for external connection |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Technics (R&D) |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0058] — PER |  | Fulfillment of standards - Insulation |  |  |  |
| --- | --- | --- | --- | --- | --- |
| All electrical and communication interfaces for internal and external connection shall fulfill [EN 60664-1]. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0323]: Normenerfüllung - BFZ, Isolation |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0063] — PER |  | Fulfillment of standards - Storage indoor- Climatic conditions |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The equipment (empty or full cabinet and/or single HW components) shall be wrapped and stored to comply with [EN 60721-3-1]: Climatic conditions: class 1K22 (Limits according standard: -25°C to +55°C for temperature; 10% to 100% for relative humidity) |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0329]: Normenerfüllung - BFZ, Lagerung [EL4-SSS-REQ-00338]: Maintainability and Maintenance - Spare Parts Storage - Climate Class [EL4-SSS-REQ-00336]: Maintainability and Maintenance - Spare Parts Storage - Effort |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | If the supplier's packaging is not sufficient and the empty cabinet is equipped with electronic HW components, the device must be packaged similarly to [PACK_INSTR]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0101] — PER |  | Fulfillment of standards - Storage indoor - Shock and vibration |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Equipment (empty or full cabinet and/or single HW components) shall be wrapped and stored to comply with [EN 60721-3-1]: Mechanical conditions: class 1M11 Stationary vibration, random 5 Hz up to 200 Hz: 0,01 (m/s²)²/Hz acceleration spectral density Duration: 120 minutes each direction Number of axes: 3 axes (vertical, transversal, longitudinal) |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0329]: Normenerfüllung - BFZ, Lagerung [EL4-SSS-REQ-00338]: Maintainability and Maintenance - Spare Parts Storage - Climate Class |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | "120 minutes each direction" is selected from [EN 60068-2-64]. If the supplier's packaging is not sufficient and the empty cabinet is equipped with electronic HW components, the device must be packaged similarly to [PACK_INSTR]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0102] — PER |  | Fulfillment of standards - Storage indoor - Resistance against active substances |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Equipment (empty or full cabinet and/or single HW components) shall be wrapped and stored to comply with [EN 60721-3-1]: Biological conditions: class 1B1 Chemically active substances: class 1C2 Mechanically active substances: class 1S11 |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0329]: Normenerfüllung - BFZ, Lagerung [EL4-SSS-REQ-00338]: Maintainability and Maintenance - Spare Parts Storage - Climate Class |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | If the supplier's packaging is not sufficient and the empty cabinet is equipped with electronic HW components, the device must be packaged similarly to [PACK_INSTR]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0064] — PER |  | Fulfillment of standards - Transport and handling - Climatic conditions |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Equipment (empty or full cabinet and/or single HW components) shall be wrapped and transported according to [EN 60721-3-2] for weather-protected transportation: Climatic conditions: class 2K12 (Limits according standard: -45°C to +70°C for temperature; 4% to 100% for relative humidity) |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0331]: Normenerfüllung - BFZ, Transport und Handhabung |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | If the supplier's packaging is not sufficient and the empty cabinet is equipped with electronic HW components, the device must be packaged similarly to [PACK_INSTR]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0103] — PER |  | Fulfillment of standards - Transport and handling - Shock and vibration |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Equipment (empty or full cabinet and/or single HW components) shall be wrapped and transported according to [EN 60721-3-2] for weather-protected transportation: Mechanical conditions: class 2M4 Stationary vibration, random Duration: 120 minutes each direction Number of axes: 3 axes (vertical, transversal, longitudinal) Shock Number of shocks: 100 in each axle direction (600 shocks total) |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0331]: Normenerfüllung - BFZ, Transport und Handhabung |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | "120 minutes each direction" is selected from [EN 60068-2-64]. If the supplier's packaging is not sufficient and the empty cabinet is equipped with electronic HW components, the device must be packaged similarly to [PACK_INSTR]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0104] — PER |  | Fulfillment of standards - Transport and handling - Resistance against active substances |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Equipment (empty or full cabinet and/or single HW components) shall be wrapped and transported according to [EN 60721-3-2] for weather-protected transportation: Biological conditions: class 2B1 Chemically active substances: class 2C2 Mechanically active substances: class 2S5 |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0331]: Normenerfüllung - BFZ, Transport und Handhabung |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | If the supplier's packaging is not sufficient and the empty cabinet is equipped with electronic HW components, the device must be packaged similarly to [PACK_INSTR]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0054] — PER |  | Fulfillment of standards - Halogen-free materials |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Used materials for cables and insulation shall be halogen-free according to [HSE Instruction]. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0032]: Einhaltung des HSE Vorgaben |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | In case of fire corrosive and toxic fumes shall be avoided. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0128] — GCR |  | Server Hardware - Minimum Installation Depth |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The racks shall provide a minimum installation depth of 100 cm for servers and network technology components. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-01131]: Server Hardware Requirements - Minimum Installation Depth |  |  |  |  |
| Status: | in negotiation |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Server cabinet |
| Verification Method: | Test |  |  | Verification Step: | system test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | This requirement is in the responsibility of the customer. Hitachi contributes only insofar that the [IPS HW] components are designed in that way, that they do not influence the required minimum installation depth in a negative way. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0129] — GCR |  | Network & Transmission Technology - [SiDiNet] and [DN2020] |  |  |  |
| --- | --- | --- | --- | --- | --- |
| At least one port shall be provided per Core Router for the [SiDiNet] channel red, [SiDiNet] channel blue and the [DN2020]. The necessary speeds and additional redundancy shall be agreed upon. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-01137]: Network & Transmission Technology - [SiDiNet] and [DN2020] |  |  |  |  |
| Status: | in negotiation |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Network cabinet |
| Verification Method: | Test |  |  | Verification Step: | system test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | == OPEN POINT == Details have to be clarified with the customer during the specification phase. [SiDiNet] refers to the (redundant) network of the security service or security technology for the [DIL]. The Data Network 2020 ([DN2020]) is responsible for access control, [UPS] status, climate control, fire alarms and switch monitoring (the transition from the safety-relevant network to DN2020 takes place in the [DC]). |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0130] — GCR |  | Network & Transmission Technology - Network Cabling |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The network cabling of the server hardware should be carried out using network cables of a uniform colour for each category (for example: red network cables are used for [SiDiNet] channel "red", blue network cables are used for [SiDiNet] channel "blue"). |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-01576]: Network & Transmission Technology - Network Cabling |  |  |  |  |
| Status: | in negotiation |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | optional |
| Originator: | Product Management |  |  | Cabinet: | Server cabinet |
| Verification Method: | Test |  |  | Verification Step: | system test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | == OPEN POINT == Details have to be clarified with the customer during the specification phase. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0147] — GCR |  | Power Supply - PDUs |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The power supply for the server hardware shall be implemented in the rack using vertically mounted [PDU]s. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-01132]: Server Hardware Requirements - Power Supply - PDUs |  |  |  |  |
| Status: | in negotiation |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | E.g. components with long lifetime, clearly defined interfaces for exchange of discontinued components, etc. (Necessary to fulfil demanding dependability and maintenance requirements.) |  |  |  |  |

## Environmental Requirements

| [GENCAB:HW-SSS:REQ:0060] — PER |  | Fulfillment of standards - Conditions of room ambient |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Regarding climatic conditions, the equipment shall be compliant to the combination of [EN 50125-3], class T1/T2 in climatic-controlled building resp. [EN 60721-3-3], class 3K20 for fully air-conditioned enclosed locations (air temperature and humidity control is used continuously to maintain the required conditions): Ambient room temperature outside cabinet: +18°C to +27°C Humidity: relative 20 % to 75 %; absolute 4 g/m³ to 15 g/m3 Elevation: class AX – up to 2000 m |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0327]: Normenerfüllung - BFZ, Klimabedingungen [EL4-SSS-REQ-00594]: Environmental Conditions - OEVE EN 50125-3 [EL4-SSS-REQ-00595]: Environmental Conditions - DIL - Altitude Class A1 [EL4-SSS-REQ-00596]: Environmental Conditions - DIL - Climate Class T2 (Indoors and Outdoors) [EL4-SSS-REQ-00336]: Maintainability and Maintenance - Spare Parts Storage - Effort |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0061] — PER |  | Fulfillment of standards - Pollution - Resistance against active substances |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Regarding mechanically active substances, the equipment shall be compliant to [EN 60721-3-3], class 3S5 for locations where precautions have been taken to minimize the presence of dust and sand and ingress of sand is prevented Biologically active substances according to [EN 60721-3-3], class 3B1 are negligible Chemically active substances according to [EN ISO 9223] class C2 is low. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0328]: Normenerfüllung - BFZ, Verschmutzung |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0105] — PER |  | Fulfillment of standards - Pollution - Macro-environmental conditions |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Regarding macro-environmental conditions for railway applications, if demanded, the equipment shall be compliant to [EN 50124-1], Annex E, Table E.1, class PD1 |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0328]: Normenerfüllung - BFZ, Verschmutzung |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0062] — PER |  | Fulfillment of standards - Operation - Shock and vibration |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Regarding mechanical conditions, the equipment shall be compliant to [EN 60721-3-3], class 3M10 for locations experiencing insignificant levels of vibration and shock. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0330]: Normenerfüllung - BFZ, Betrieb: Stoß und Vibration |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0057] — PER |  | Fulfillment of standards - Protection classes by housing |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The cabinet shall fulfill IP20 according to [EN 60529]. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0322]: Normenerfüllung - BFZ, Schutzarten durch Gehäuse [EL4-SSS-REQ-00780]: Protection Rating - DIL-CU Components [EL4-SSS-REQ-00781]: Protection Rating - DC Requirements |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0059] — PER |  | Fulfillment of standards - EMC |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Regarding EMC, the equipment shall be compliant to [EN 61000-6-2], [EN 61000-6-4] for industrial environments and [EN 50121-4] for railway applications. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0326]: Normenerfüllung - BFZ, Elektromagnetische Verträglichkeit [EL4-SSS-REQ-00598]: EMC - Testing - System Level [EL4-SSS-REQ-00599]: EMC - Testing - Subsystem/Component Level [EL4-SSS-REQ-00601]: EMI - EN 50121-4 |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | See also definitions and requirements regarding EMC in [ELEKTRA Environmental Conditions] chapter 3.2.1.2 and [DSTW Anforderungen Analyse]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0069] — PER |  | Cabinet WEEE |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The HW components shall be compliant to [WEEE]. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0032]: Einhaltung des HSE Vorgaben |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0070] — PER |  | Cabinet RoHS |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The HW components shall be compliant to [RoHS]. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0032]: Einhaltung des HSE Vorgaben [EL4-SSS-REQ-00604]: EMS - DC Server [EL4-SSS-REQ-00777]: Environmental Protection - Hazardous Materials [EL4-SSS-REQ-00778]: Environmental Protection - Materials in Case of Fire |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0071] — PER |  | Cabinets REACH |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The HW components shall be compliant to [REACH]. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0032]: Einhaltung des HSE Vorgaben [EL4-SSS-REQ-00777]: Environmental Protection - Hazardous Materials [EL4-SSS-REQ-00778]: Environmental Protection - Materials in Case of Fire |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0116] — PER |  | Sensor for environmental parameters |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The server cabinet shall be equipped with a temperature and humidity sensor and the status message shall be provided to the PDU. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00758]: Environmental Conditions - Monitoring of Warning and Limit Values [GENCAB:HW-SSS:IDJ:ID:0012]: Sensor for environmental parameters |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Server cabinet |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0123] — GCR |  | Fulfillment of Standard EN 50126 |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The requirements according to [EN 50126-1] shall be fulfilled for Basic Integrity components. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00303]: Fulfillment of Standard EN 50126 [EL4-SSS-REQ-00685]: Safety - Integrity Levels - Interface - DDSP, PS |  |  |  |  |
| Status: | in negotiation |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Analysis Test |  |  | Verification Step: | system test safety analysis |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | IPS as a whole is NonSIL Two power interfaces are SIL Basic Integrity (BI) Compliance with the requirements of [EN 50126-1] is documented in the [RAM PLAN] and in the [SAFETY PLAN]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0142] — GCR |  | Cooling Concept - Cabinet |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The specific heat dissipation of each cabinet must be calculated and provided for the superimposed cooling concept, and the direction of the cooling air flow must be defined. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-01119]: Cooling Concept - Topics [EL4-SSS-REQ-01122]: Cooling Concept - Air Flow |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | system test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

## Safety

| [GENCAB:HW-SSS:REQ:0080] — SAR |  | Compliance with CENELEC standards |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The design, testing and qualification of the cabinet shall be done according to [EN 50129]. |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0295]: Einhaltung der CENELEC Standards [EL4-SSS-REQ-00305]: Fulfillment of Standard EN 50129 [EL4-SSS-REQ-00688]: Safety - Integrity Levels - Certificates |  |  |  |  |
| Status: | to be descoped |  |  | Stability: | stable |
| Target Release: | BFZ-2.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | review |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | It is not intended to use the product in the area near the track. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0075] — SAR |  | Failure rate |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The failure rate of components shall enable the projects to fulfill their individual hazard rate targets by using their safety concept (up to SIL4). |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0299]: Gefährdungsrate [EL4-SSS-REQ-00305]: Fulfillment of Standard EN 50129 [EL4-SSS-REQ-00316]: Reliability - Safe Design [EL4-SSS-REQ-00317]: Reliability - Evidence by Calculation [EL4-SSS-REQ-00683]: Safety - Integrity Levels - Interface - Adjacent Systems [EL4-SSS-REQ-00686]: Safety - Integrity Levels - Development DIL |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-2.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Analysis |  |  | Verification Step: | RAM Analysis |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Failure rate: - ELEKTRA HW according to [Hazard Rate Elektra 2.x] - ILP HW according to [Sicherheitsnachweis ILP] - 200.000h for a 1oo1 architecture according to TAS Platform Safety Concept (see [EoC Server]) |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0140] — SAR |  | Split-brain - connection between HW components |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The ToR Switches of the Server Cabinet shall be connected to the Core Routers in the Network Cabinet in accordance with the [SB_Concept]. |  |  |  |  |  |
| Origin: | [EL4:IDJ-RA:ID:0037]: Split-brain avoidance |  |  |  |  |
| Status: | in negotiation |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review Analysis |  |  | Verification Step: | review analysis |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | The Service Links shall be “crossed” |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0141] — SAR |  | Split-brain - connection between HW components & Geo interconnection |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The Core routers shall be connected to the geo- interconnection network in accordance with the [SB_Concept] |  |  |  |  |  |
| Origin: | [EL4:IDJ-RA:ID:0037]: Split-brain avoidance |  |  |  |  |
| Status: | in negotiation |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Network cabinet |
| Verification Method: | Inspection/Review Analysis |  |  | Verification Step: | review analysis |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | The Service Link in one geo-site shall be a "crossed" to eliminate the split-brain in the double fault situations of core routers |  |  |  |  |

## Physical Security

| [GENCAB:HW-SSS:REQ:0084] — SER |  | Lock for cabinet |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The cabinet shall be equipped with door locks. The locks of the racks shall be able to be configurable differently (e.g. different keys). |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0128]: Schutz vor unbefugter Nutzung von Diagnoseschnittstellen [BFZ-3.x:SRS:REQ:0156]: Netzwerkgeräte: Schutz gegen Manipulation [EL4-SSS-REQ-00790]: Employee Protection - System Protection - Concept |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: | [IPS_EoC_IEC_62443-4-2] HDR 3.11 – Physical tamper resistance and detection - SL:2 [IPS_EoC_IEC_62443-4-2] NDR 3.11 – Physical tamper resistance and detection - SL:2 |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0085] — SER |  | Open door sensor |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The cabinet shall be equipped with open door sensors and the status message shall be provided to the PDU. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0079]: Security Log: Protokollierung von physischen Aktionen [BFZ-3.x:SRS:REQ:0128]: Schutz vor unbefugter Nutzung von Diagnoseschnittstellen [BFZ-3.x:SRS:REQ:0156]: Netzwerkgeräte: Schutz gegen Manipulation [EL4-SSS-REQ-00790]: Employee Protection - System Protection - Concept |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: | EL4-IPS-SSS-REQ-90017 EL4-IPS-SSS-REQ-90018 |  |  |  |  |
| IEC: | [IPS_EoC_IEC_62443-4-2] HDR 3.11 – Physical tamper resistance and detection - SL:2 [IPS_EoC_IEC_62443-4-2] NDR 3.11 – Physical tamper resistance and detection - SL:2 |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0110] — SER |  | Cabinet side panels |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The removable side panels shall be lockable from inside. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0128]: Schutz vor unbefugter Nutzung von Diagnoseschnittstellen [BFZ-3.x:SRS:REQ:0156]: Netzwerkgeräte: Schutz gegen Manipulation [EL4-SSS-REQ-00790]: Employee Protection - System Protection - Concept |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: | [IPS_EoC_IEC_62443-4-2] HDR 3.11 – Physical tamper resistance and detection - SL:2 [IPS_EoC_IEC_62443-4-2] NDR 3.11 – Physical tamper resistance and detection - SL:2 |  |  |  |  |
| Comments: | The side panels are removable for better installation and maintenance handling. |  |  |  |  |

## Cyber Security

| [GENCAB:HW-SSS:REQ:0118] — FUR |  | Performance data |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The HW components (network components and servers) shall provide interfaces to transmit performance data remotely. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0036]: Leistungsdaten - Erkennen von Anomalien im System [EL4-SSS-REQ-00319]: Reliability - Error Reporting - OMC |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Interface of the servers are BMC e.g. iLO for HP and IDRAC for Dell. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0119] — SER |  | Secure Boot |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The HW components (router, switches and servers) shall support secure boot. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0129]: Secure-Boot |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: | EL4-IPS-SSS-REQ-90011 EL4-IPS-SSS-REQ-90012 EL4-IPS-SSS-REQ-90013 EL4-IPS-SSS-REQ-90014 EL4-IPS-SSS-REQ-90015 EL4-IPS-SSS-REQ-90016 |  |  |  |  |
| IEC: | [IPS_EoC_IEC_62443-4-2] HDR 3.14 – Integrity of the boot process - SL:1 [IPS_EoC_IEC_62443-4-2] HDR 3.14 (1) – Authenticity of the boot process - SL:2 [IPS_EoC_IEC_62443-4-2] NDR 3.14 – Integrity of the boot process - SL:1 [IPS_EoC_IEC_62443-4-2] NDR 3.14 (1) – Authenticity of the boot process - SL:2 |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0120] — SER |  | Configuration Interface |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The HW components (router, switches and servers) shall provide interfaces to configure, maintain and modify the network and security configurations. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0163]: Schnittstelle für Netzwerk- und Sicherheitskonfigurationseinstellungen |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: | [IPS_EoC_IEC_62443-4-2] CR 7.6 – Network and security configuration settings - SL:1 |  |  |  |  |
| Comments: |  |  |  |  |  |

## Dependability Requirements

| [GENCAB:HW-SSS:REQ:0024] — DPR |  | Availability - Internal network |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The network availability of a location shall be at least 99.9999%. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0195]: Verfügbarkeit eines BFZ-Systems gesamt (Klasse 1) [BFZ-3.x:SRS:REQ:0196]: Verfügbarkeit eines aktiven BFZ-Subsystems gesamt (Klasse 1) [BFZ-3.x:SRS:REQ:0197]: Verfügbarkeit eines passiven BFZ-Subsystems gesamt (Klasse 1) [BFZ-3.x:SRS:REQ:0198]: Aufteilung Verfügbarkeit BFZ-System gesamt [BFZ-3.x:SRS:REQ:0199]: Aufteilung Verfügbarkeit aktives BFZ-Subsystem gesamt [BFZ-3.x:SRS:REQ:0200]: Aufteilung Verfügbarkeit passives BFZ-Subsystem gesamt [EL4-SSS-REQ-00307]: Availability - Network - Overall [GENCAB:HW-SSS:IDJ:ID:0010]: Availability - Internal network |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Network cabinet |
| Verification Method: | Analysis |  |  | Verification Step: | RAM Analysis |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | The HW architecture design follows the network design as specified by the supplier according to [BFZ Low Level Design]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0031] — DPR |  | Single Failure - HW component no consequences |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A single failure of a HW component must not lead to any operational restrictions. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0194]: Keine betriebliche Auswirkung bei einem Einfachfehler im BFZ-System [EL4-SSS-REQ-00316]: Reliability - Safe Design [EL4-SSS-REQ-00323]: Reliability - Failure of a server |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Addresses single failures of LRUs. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0081] — DPR |  | Single Failure - Diagnosis |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A failure of a HW component shall be diagnosed. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0194]: Keine betriebliche Auswirkung bei einem Einfachfehler im BFZ-System [EL4-SSS-REQ-00990]: Reliability - Single HW Failure - Diagnosis [GENCAB:HW-SSS:IDJ:ID:0011]: Single failure - Diagnosis |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Addresses single failures of LRUs. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0088] — DPR |  | Compute servers - High availability |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Compute servers within a server cabinet shall provide an availability high enough to assure a class 1 availability. This means in particular an availability of: - 99.9998 % (MTTR = 6 h) - 99.9996 % (MTTR = 10 min) - 99.9996 % (MTTR = 2 min) |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) [EL4-SSS-REQ-00407]: Availability distribution of [DIL-CU] |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Server cabinet |
| Verification Method: | Test |  |  | Verification Step: | endurance test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | No operational consequences in case of a router, power supply, disk or fan failure, provided this is also supported by SW. Equal availabilities with different MTTR values are derived from customer requirements stating that outages with MTTR =2 min may occur more often per N years than outages with MTTR = 10 min. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0089] — DPR |  | Switch server cabinet - High availability of Subsystem |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The two switches within a server cabinet shall provide an availability high enough to assure a class 2 availability of the active respectively passive Subsystem. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Server cabinet |
| Verification Method: | Test |  |  | Verification Step: | endurance test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | No operational consequences in case of a switch failure, provided this is also supported by SW. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0090] — DPR |  | Switch server cabinet - High availability of CNs |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The two switches within a server cabinet shall provide an availability high enough to assure a class 2 availability of a master respectively slave CN (Computing Node). |  |  |  |  |  |
| Origin: | [GENCAB:HW-SSS:IDJ:ID:0003]: Cabinet components |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: |  |  |  | Priority: | optional |
| Originator: | RAM |  |  | Cabinet: | Server cabinet |
| Verification Method: | Test |  |  | Verification Step: | endurance test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | No operational consequences in case of a switch failure, provided this is also supported by SW. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0091] — DPR |  | Storage servers - High availability |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Storage servers within a server cabinet shall provide an availability high enough to assure a class 2 availability of the active respectively passive OMC Subsystem. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Server cabinet |
| Verification Method: | Test |  |  | Verification Step: | endurance test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | No operational consequences in case of a router, power supply, disk or fan failure, provided this is also supported by SW. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0092] — DPR |  | Control servers - High availability |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The control servers in different server cabinets shall provide an availability high enough to assure a class 2 availability of the active respectively passive OMC Subsystem. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Server cabinet |
| Verification Method: | Test |  |  | Verification Step: | endurance test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | No operational consequences in case of a router, power supply, disk or fan failure, provided this is also supported by SW. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0093] — DPR |  | Storage servers in different server cabinets - High availability |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Storage servers in different server cabinets at the same location shall provide an availability high enough to assure a class 2 availability of the active respectively passive OMC Subsystem. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Server cabinet |
| Verification Method: | Test |  |  | Verification Step: | endurance test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | No operational consequences in case of a router, power supply, disk or fan failure, provided this is also supported by SW. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0094] — DPR |  | Compute servers in different server cabinets - High availability |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Compute servers in different server cabinets at the same location shall provide an availability high enough to assure a class 2 availability of the active respectively passive OMC Subsystem. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Server cabinet |
| Verification Method: | Test |  |  | Verification Step: | endurance test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | No operational consequences in case of a router, power supply, disk or fan failure, provided this is also supported by SW. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0095] — DPR |  | Failure of a connection does not affect other connections |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A failure of one connection shall not affect the operational availability of the other connections. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) [EL4-SSS-REQ-00326]: Reliability - Failure of a Connection |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Refers to a network connection |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0096] — DPR |  | Router resp. Switches network cabinet - High availability |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The routers resp. switches within a network cabinet shall provide an availability high enough to assure a class 2 availability of the active respectively passive OMC Subsystem. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Network cabinet |
| Verification Method: | Test |  |  | Verification Step: | endurance test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | No operational consequences in case of a router resp. switch failure. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0097] — DPR |  | Failure of a server does not affect other servers |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A failure of one server shall not affect the operational availability of other servers. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) [EL4-SSS-REQ-00323]: Reliability - Failure of a server |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Server cabinet |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0098] — DPR |  | Failure of a PDU shall be tolerable |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A failure of a PDU shall not have operational consequences. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) [EL4-SSS-REQ-00324]: Reliability - Failure of a PDU |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0099] — DPR |  | Failure of a UPS shall be tolerable |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A failure of a UPS shall not have operational consequences. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) [EL4-SSS-REQ-00325]: Reliability - Failure of a UPS |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | RAM |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0083] — DPR |  | Power supply - Redundancy - Availability |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The three phases of each UPS shall be connected within the cabinet in a way to tolerate HW failures. An outage of one phase shall have no impact on other phases. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0361]: Separater Phasenschutz [BFZ-3.x:SRS:REQ:0392]: Separater Phasenschutz [EL4-SSS-REQ-00481]: Power Supply - Support of Data Center Power Supply [EL4-SSS-REQ-00324]: Reliability - Failure of a PDU [EL4-SSS-REQ-00308]: Power supply - UPS Design |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | See section 3.2 "Regeln für die Phasenaufteilung" in the document [Rechnerschrank D6 Generisch]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0044] — DPR |  | Power supply - Redundancy - Availability of related components |  |  |  |
| --- | --- | --- | --- | --- | --- |
| All critical HW components which are related to availability (Server, Router, Switches), shall be equipped with two or more independent power supplies. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0319]: Stromversorgung -Redundanz - Verfügbarkeitsrelevante Komponenten [EL4-SSS-REQ-00481]: Power Supply - Support of Data Center Power Supply [EL4-SSS-REQ-00309]: Power supply - Availability related Components - Redundancy |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0113] — DPR |  | Server cabinet - Connection to switches |  |  |  |
| --- | --- | --- | --- | --- | --- |
| A server within a server cabinet shall be connected to each switch within this server cabinet. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) [EL4-SSS-REQ-00310]: Availability - Switches - Connection with Servers |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | A twofold redundant connection from each server within a server cabinet to each switch within the server cabinet does not follow from this requirement. It needs to be explicitly required. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0114] — DPR |  | Cabinet - Connection to routers of the network cabinet I |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The two switches for the internal network within a cabinet shall be connected with the two routers of the network cabinet. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0202]: Verfügbarkeit Zelle eines aktiven BFZ-Subsystems (Klasse 2) [BFZ-3.x:SRS:REQ:0203]: Verfügbarkeit Zelle eines passiven BFZ-Subsystems (Klasse 2) [EL4-SSS-REQ-00311]: Availability - Switches - Internal Network - Connection with Routers |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0115] — DPR |  | Cabinet - Connection to routers of the network cabinet II |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The two switches for the external network within a cabinet shall be connected with the two routers in the network cabinet. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0023]: Georedundanz - Wiederverwendbarkeit für andere Produkte [EL4-SSS-REQ-00311]: Availability - Switches - Internal Network - Connection with Routers [GENCAB:HW-SSS:IDJ:ID:0003]: Cabinet components |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | optional |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0133] — DPR |  | Reliability - Replacement of HW Component - No operational Impact |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Replacement of failed/defective components shall have no adverse effect on the operation and reliability of the system as a whole. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00322]: Reliability - Replacement of HW Component - No operational Impact |  |  |  |  |
| Status: | to be descoped |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Analysis Test |  |  | Verification Step: | analysis system test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

## Industrialization

| [GENCAB:HW-SSS:REQ:0014] — MDR |  | Uniform branding |  |  |  |
| --- | --- | --- | --- | --- | --- |
| All hardware components shall have a uniform appearance and company branding. |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0208]: Einheitliches Branding [GENCAB:HW-SSS:IDJ:ID:0002]: Uniform Branding |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-2.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | The color of the cabinet corresponds to the color of the Elektra 2.x or the closest possible one of the supplier. For Elektra 2.x color, see [ELEKTRA 2.x Schrank]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0082] — MDR |  | Labeling |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Labeling shall be done according to [Industrialisierungsvorgaben], [EN 61010-1] and [EN 62368-1] and shall be applied to the smallest replaceable unit. Additionally, the [MAC] addresses shall be part of the labels. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0321]: Normenerfüllung - BFZ, Produktsicherheit [EL4-SSS-REQ-00339]: Maintainability and Maintenance - Labelling - Data [EL4-SSS-REQ-00340]: Maintainability and Maintenance - Labelling - Units [EL4-SSS-REQ-00342]: Maintainability and Maintenance - Labelling - QR-Code - Format [EL4-SSS-REQ-00343]: Maintainability and Maintenance - Labelling - Serial Number [EL4-SSS-REQ-00350]: Maintainability and Maintenance - Process - Access |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | In case of NIC card replacement the label shall be modified. Examples of the smallest replaceable unit: - Power supply units - Lightning protection - Separately mountable parts by the supplier - Server |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0143] — MDR |  | Maintainability and Maintenance - Labelling - Units |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Labelling shall be applied to the smallest replaceable unit, for example: - Power supply units - Lightning protection - Separately mountable parts by the supplier - Server |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00340]: Maintainability and Maintenance - Labelling - Units |  |  |  |  |
| Status: | to be descoped |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

## Product Safety

| [GENCAB:HW-SSS:REQ:0051] — GCR |  | Fulfillment of standards - Product safety I |  |  |  |
| --- | --- | --- | --- | --- | --- |
| All HW components shall fulfill requirements for electrical safety according to [EN 61010-1]. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0321]: Normenerfüllung - BFZ, Produktsicherheit [EL4-SSS-REQ-00566]: Maintainability and Maintenance - Employee Protection - Product Safety [EL4-SSS-REQ-00785]: Employee Protection - Preventive Services/Forces |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Detailed requirements see [Generic HW Standards]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0050] — MDR |  | Fulfillment of standards - Product safety II |  |  |  |
| --- | --- | --- | --- | --- | --- |
| All HW components shall fulfill requirements for electrical safety according to [EN 62368-1]. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0321]: Normenerfüllung - BFZ, Produktsicherheit [EL4-SSS-REQ-00785]: Employee Protection - Preventive Services/Forces |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Detailed requirements see [Generic HW Standards]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0078] — SAR |  | Compliance with employee protection regulations |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The server and the network cabinets shall comply to [OEBB R10]. |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0297]: Einhaltung Arbeitnehmerschutzbestimmungen [EL4-SSS-REQ-00784]: Employee Protection - Regulations [EL4-SSS-REQ-01476]: Maintainability and Maintenance - Employee Protection - R10 |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-2.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Detailed requirements see [Generic HW Standards]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0065] — SAR |  | Declarations of Conformity |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Each cabinet shall be developed in a way to allow issuing a declaration of conformity. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0324]: Konformitätserklärung - BFZ [BFZ-3.x:SRS:REQ:0325]: Erfüllung Normen und Konformität - Zusatzkomponenten |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0066] — PHR |  | Fulfillment of standards - HSE Requirements |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The design, testing and qualification of the cabinets shall be done according to [HSE Instruction]. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0032]: Einhaltung des HSE Vorgaben |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | review HW System/Integration Test qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0076] — PHR |  | Compliance with laws and regulations I |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The server and network cabinets shall be compliant with the following Austrian laws and regulations in the version valid at the time of admission: - Elektrotechnikgesetz 1992 - ETG 1992 - Elektrotechnikverordnung 2020 - ETV 2020 - Elektroschutzverordnung 2012 - ESV 2012 |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0296]: Einhaltung Gesetze und Verordnungen |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-2.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Maschinensicherheitsverordnung (corresponds to Maschinen-Richtlinie 2006/42/EC) is not applicable because there are no moving parts in the cabinet (cabinet or component fans e.g. do not fall within the scope). |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0077] — PHR |  | Compliance with laws and regulations II |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The server and network cabinets shall be compliant with the following laws and regulations in the version valid at the time of admission: - Elektromagnetische Verträglichkeitsverordnung 2015 - EMVV 2015 (corresponds to EMV-Richtlinie 2014/30/EU) - Niederspannungsgeräteverordnung 2015 - NspGV 2015 (corresponds to EMV-Richtlinie 2014/35/EU) - [Ecodesign Directive 2019/424/EU] (Lot 9) |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0296]: Einhaltung Gesetze und Verordnungen [EL4-SSS-REQ-00604]: EMS - DC Server |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | BFZ-2.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test qualification test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Maschinensicherheitsverordnung (corresponds to Maschinen-Richtlinie 2006/42/EC) is not applicable because of no moving parts in the cabinet (cabinet or component fans e.g. do not fall within the scope). |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0125] — SAR |  | Safety - Maintenance - SRACs |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Any additional expenses, efforts or [SRAC]s for the maintenance personnel of the customer as a result of the [CENELEC] phases 5-10 shall be agreed between the supplier and the customer. The phases are Architecture and hardware specification, design and implementation, manufacturer, integration, system validation and system acceptance. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00691]: Safety - Maintenance - SRACs |  |  |  |  |
| Status: | to be descoped |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | review |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0126] — SAR |  | Safety - Maintenance - Activities |  |  |  |
| --- | --- | --- | --- | --- | --- |
| It shall not be possible for planned maintenance activities to result in unsafe conditions in terms of safety or operation. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00692]: Safety - Maintenance - Activities |  |  |  |  |
| Status: | to be descoped |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Analysis Test |  |  | Verification Step: | analysis system test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0127] — SAR |  | Safety - Maintenance - Exchange of elements |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The exchange of systems, subsystems or components of the customer in server racks of the supplier shall not require any safety-related training or education. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00693]: Safety - Maintenance - Exchange of FES elements |  |  |  |  |
| Status: | to be descoped |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | integration test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | The customer does not consider [DIL] (basic) training according to the supplier's concept as safety-related training or education. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0131] — GCR |  | Grounding and Surge Protection - Grounding Concept |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The supplier shall create, agree with the customer and implement a grounding concept in accordance with [EN 50310] and [EN 50122]. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00605]: Grounding and Surge Protection - Grounding Concept |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Analysis |  |  | Verification Step: | analysis |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | The grounding concept must be defined at the system level. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0132] — ECR |  | Grounding and Surge Protection |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The system shall be connected to the existing grounding system ensuring that no adverse interactions or back‑effects can occur. (E.g. Filter capacitances against earth can also generate overcurrents over a longer period of time, which can lead to a trip by the RCD). |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00606]: Grounding and Surge Protection - DIL Integration |  |  |  |  |
| Status: | in negotiation |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Analysis |  |  | Verification Step: | analysis |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Relevant back‑effects include potential equalization currents, return currents from traction power systems, lightning‑induced or switching-related overvoltages, electromagnetic interference, ground loop effects, and any unintended coupling that may impact the functional integrity of the DSTW or adjacent systems. Note: Applies also to the Computing Centre. == OPEN POINT == Existing grounding system unknown. |  |  |  |  |

## Performance

| [GENCAB:HW-SSS:REQ:0049] — PRR |  | Network bandwidth between locations |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The network cabinet interface, at least two SFP modules per network cabinet, shall support at least a bandwidth of 50Gbit/sec per line between locations. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0029]: Georedundanz - Netzwerkbandbreite [EL4-SSS-REQ-00551]: Network [DC] - General Requirements |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Network cabinet |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | The HW architecture design follows the network design as specified by the supplier according to [BFZ Low Level Design]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0111] — PRR |  | Network bandwidth within one location |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The network cabinet interface shall support at least a bandwidth of 100Gbit/sec within one location. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0029]: Georedundanz - Netzwerkbandbreite |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Network cabinet |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | The HW architecture design follows the network design as specified by the supplier according to [BFZ Low Level Design]. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0005] — PRR |  | Network cabinet components |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The network cabinet shall carry at least the following components: - 2 Routers - 10 Switches - 2 Power Distribution Units (PDU) |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0166]: Anzahl USt und Weichen [BFZ-2.x:SRS:REQ:0187]: Dauer Generalabfrage [BFZ-3.x:SRS:REQ:0023]: Georedundanz - Wiederverwendbarkeit für andere Produkte [BFZ-3.x:SRS:REQ:0189]: Georedundanz - Anzahl der Standorte [GENCAB:HW-SSS:IDJ:ID:0003]: Cabinet components |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Technics (R&D) |  |  | Cabinet: | Network cabinet |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0006] — PRR |  | Server cabinet components |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The server cabinet shall carry at least the following components: - 4 Switches - 1 KVM - 15 Server Compatible with TAS Platform Safety Case - 2 Power Distribution Units (PDU) |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0166]: Anzahl USt und Weichen [BFZ-2.x:SRS:REQ:0187]: Dauer Generalabfrage [BFZ-3.x:SRS:REQ:0023]: Georedundanz - Wiederverwendbarkeit für andere Produkte [BFZ-3.x:SRS:REQ:0189]: Georedundanz - Anzahl der Standorte [GENCAB:HW-SSS:IDJ:ID:0003]: Cabinet components |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Technics (R&D) |  |  | Cabinet: | Server cabinet |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | To fulfill the required performance, the Server configuration shall be as follows - or higher: - 12x64GB RAM (OMC: 6x64GB) - AMD 3,25GHz; 32 Core (64 Threads) CPU - 8x960GB SATA SSD (OMC: 3 Server with 8 SSD, 12 Server with 2 SSD) - 2x2 Ethernet Ports 10Gbit/sec - 1x4 Ethernet Ports 1Gbit/sec Regarding compatibility see [EoC Server]. |  |  |  |  |

## Technical Requirements

| [GENCAB:HW-SSS:REQ:0046] — GCR |  | Power supply and power consumption |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The power consumption of three server cabinets plus one network cabinet shall be limited to 22,2kW. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0344]: Georedundanz - Stromversorgung Leistungsgrenzwerte [EL4-SSS-REQ-00481]: Power Supply - Support of Data Center Power Supply |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0011] — TIR |  | Power supply |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The cabinet shall be developed to support two independent three phase power supplies. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0361]: Separater Phasenschutz [EL4-SSS-REQ-00481]: Power Supply - Support of Data Center Power Supply [EL4-SSS-REQ-00422]: Power supply - PDU Design |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-2.0 IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | OEBB will provide two separate UPS. |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0138] — DPR |  | Power Supply - Non-Availability related Components - Monitoring and Backup |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Components not related to availability shall be powered by a single power supply, but in that case monitoring and backup equipment for automatic switch-over shall be provided. |  |  |  |  |  |
| Origin: | [EL4-SSS-REQ-00315]: Power Supply - Non-Availability related Components - Monitoring and Backup |  |  |  |  |
| Status: | draft |  |  | Stability: | stable |
| Target Release: | IPSS OBB 1.0.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Test |  |  | Verification Step: | system test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

## Functional Requirements

| [GENCAB:HW-SSS:REQ:0007] — FUR |  | System architecture |  |  |  |
| --- | --- | --- | --- | --- | --- |
| To control sub-stations directly and to ensure a problem free migration phase for changeover from OMC 2.0 to OMC 3.0, the following ethernet interfaces shall be provided: - Copper - Fiber optic |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0164]: 2-stufige Systemarchitektur [BFZ-3.x:SRS:REQ:0336]: Georedundanz - Migrationskonzept per Zelle |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-2.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0018] — FUR |  | Compatibility between internal components |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Each component shall guarantee compatibility with previous versions of all its interfaces within the OMC, if required. The number of combinations shall be kept as low as possible. The identification of the entire system shall be defined in the scope of change. |  |  |  |  |  |
| Origin: | [BFZ-2.x:SRS:REQ:0302]: Rückwärtskompatibilität |  |  |  |  |
| Status: | descoped |  |  | Stability: | stable |
| Target Release: | BFZ-2.0.2 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Generic |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: |  |  |  |  |  |

| [GENCAB:HW-SSS:REQ:0067] — FUR |  | Outposts, Number of workplaces |  |  |  |
| --- | --- | --- | --- | --- | --- |
| The network cabinet shall provide interfaces (Ethernet) to support up to 70 EBO 2 OMC workplaces. |  |  |  |  |  |
| Origin: | [BFZ-3.x:SRS:REQ:0187]: Georedundanz - Maximale Anzahl der EBO2 OMC Arbeitsplätze |  |  |  |  |
| Status: | approved |  |  | Stability: | stable |
| Target Release: | BFZ-3.0 |  |  | Priority: | mandatory |
| Originator: | Product Management |  |  | Cabinet: | Network cabinet |
| Verification Method: | Inspection/Review |  |  | Verification Step: | HW System/Integration Test |
| See also: |  |  |  |  |  |
| IEC: |  |  |  |  |  |
| Comments: | Actually one EBO cabinet consists of up to 5 EBO workplaces. |  |  |  |  |

## Open Issue

- For ÖBB [DIL] indoor installations, racks/ cabinets and ToR switches may be provided by the customer. In such cases, installation shall be carried out using the customer-supplied racks.

- The requirements documented in the Ed 05 shall be reviewed and analysed in order to allocate generic part for the common Label IPS 40.0.0 of the IPS Subsystem. In the next iteration a new attribute shall be introduced and included in the document.

- The Requirements derived from the [DIL] input remain classified as “stable” in order to ensure consistency and traceability with the corresponding top – level [DIL] SSS requirements, which are also defined as “stable”. However, it shall be considered that due to the currently non-finalized contract and feature list these requirements may still be subject to changes during the ongoing requirements definition phase.

- The Split -Brain avoidance & Cabinet - Connection to routers requirements are currently under discussion and not yet finalized. It is a subject to review and agreement within a broader expert group, including IPS specialists and Nokia network supplier. The requirement status is “in negotiation” and will be updated to “Accepted” only after a formal decision has been reached.

- [GENCAB:HW-SSS:REQ:0114] - Cabinet - Connection to routers of the network cabinet I

- [GENCAB:HW-SSS:REQ:0115] - Cabinet - Connection to routers of the network cabinet II

- [GENCAB:HW-SSS:REQ:0140] - Split-brain - connection between HW components

- [GENCAB:HW-SSS:REQ:0141] - Split-brain - connection between HW components & Geo interconnection

- The following requirements were introduced during the document review and have not yet completed stakeholders review. They remain “in negotiation” status and will be finalized in the subsequent revision:

- [GENCAB:HW-SSS:REQ:0144] - Double doors

- [GENCAB:HW-SSS:REQ:0145] - Minimum Useful Life - COTS Components

- [GENCAB:HW-SSS:REQ:0146] - Minimum supply period - spare parts

- [GENCAB:HW-SSS:REQ:0147] - Power Supply - PDUs

- A misalignment exists between the SEMP, CMP, RMP and Safety Plan regarding Target release “IPSS OBB 1.0.0”, which is defined on the system Level. Since SEMP, CMP are intended as a baseline input for subsequent planning artifacts, synchronisation is required.

- The minimum useful life requirement for HW components is inconsistent across the products: (7 years for [DIL] and 25 years for [OMC]):

- [GENCAB:HW-SSS:REQ:0122] - Minimum Useful Life - Continuous Utilisation

- [GENCAB:HW-SSS:REQ:0008] - Product lifecycle

- Requirements marked as “customer responsibility” shall be set “in negotiation” status and review and discussed again prior to final release of the document.

- [GENCAB:HW-SSS:REQ:0128] - Server Hardware - Minimum Installation Depth

- Classification is required regarding the consistency between the non-SIL classification of the IPS hardware and the requirements defining two power interfaces with Basic Integrity (BI). It shall be determined whether BI is applicable to this hardware scope and which evidences is required to demonstrate compliance on the HW level.

- [GENCAB:HW-SSS:REQ:0123] - Fulfillment of Standard EN 50126

- Internal and external networks are not explicitly defined in the current architecture. The network segmentation and classification of the communication paths shall be defined.

- [GENCAB:HW-SSS:REQ:0114] - Cabinet - Connection to routers of the network cabinet I

- [GENCAB:HW-SSS:REQ:0115] - Cabinet - Connection to routers of the network cabinet II

- index of requirements

GENCAB:HW-SSS:REQ:0001	35

GENCAB:HW-SSS:REQ:0002	35

GENCAB:HW-SSS:REQ:0003	45

GENCAB:HW-SSS:REQ:0004	45

GENCAB:HW-SSS:REQ:0005	84

GENCAB:HW-SSS:REQ:0006	85

GENCAB:HW-SSS:REQ:0007	87

GENCAB:HW-SSS:REQ:0008	37

GENCAB:HW-SSS:REQ:0009	39

GENCAB:HW-SSS:REQ:0010	36

GENCAB:HW-SSS:REQ:0011	86

GENCAB:HW-SSS:REQ:0012	46

GENCAB:HW-SSS:REQ:0014	76

GENCAB:HW-SSS:REQ:0018	88

GENCAB:HW-SSS:REQ:0024	65

GENCAB:HW-SSS:REQ:0027	39

GENCAB:HW-SSS:REQ:0028	40

GENCAB:HW-SSS:REQ:0031	66

GENCAB:HW-SSS:REQ:0044	73

GENCAB:HW-SSS:REQ:0046	86

GENCAB:HW-SSS:REQ:0049	83

GENCAB:HW-SSS:REQ:0050	78

GENCAB:HW-SSS:REQ:0051	77

GENCAB:HW-SSS:REQ:0054	52

GENCAB:HW-SSS:REQ:0057	56

GENCAB:HW-SSS:REQ:0058	48

GENCAB:HW-SSS:REQ:0059	57

GENCAB:HW-SSS:REQ:0060	54

GENCAB:HW-SSS:REQ:0061	55

GENCAB:HW-SSS:REQ:0062	56

GENCAB:HW-SSS:REQ:0063	49

GENCAB:HW-SSS:REQ:0064	50

GENCAB:HW-SSS:REQ:0065	79

GENCAB:HW-SSS:REQ:0066	79

GENCAB:HW-SSS:REQ:0067	88

GENCAB:HW-SSS:REQ:0069	57

GENCAB:HW-SSS:REQ:0070	58

GENCAB:HW-SSS:REQ:0071	58

GENCAB:HW-SSS:REQ:0075	61

GENCAB:HW-SSS:REQ:0076	80

GENCAB:HW-SSS:REQ:0077	80

GENCAB:HW-SSS:REQ:0078	78

GENCAB:HW-SSS:REQ:0080	60

GENCAB:HW-SSS:REQ:0081	66

GENCAB:HW-SSS:REQ:0082	76

GENCAB:HW-SSS:REQ:0083	73

GENCAB:HW-SSS:REQ:0084	62

GENCAB:HW-SSS:REQ:0085	63

GENCAB:HW-SSS:REQ:0086	40

GENCAB:HW-SSS:REQ:0087	41

GENCAB:HW-SSS:REQ:0088	67

GENCAB:HW-SSS:REQ:0089	67

GENCAB:HW-SSS:REQ:0090	68

GENCAB:HW-SSS:REQ:0091	68

GENCAB:HW-SSS:REQ:0092	69

GENCAB:HW-SSS:REQ:0093	69

GENCAB:HW-SSS:REQ:0094	70

GENCAB:HW-SSS:REQ:0095	70

GENCAB:HW-SSS:REQ:0096	71

GENCAB:HW-SSS:REQ:0097	71

GENCAB:HW-SSS:REQ:0098	72

GENCAB:HW-SSS:REQ:0099	72

GENCAB:HW-SSS:REQ:0100	47

GENCAB:HW-SSS:REQ:0101	49

GENCAB:HW-SSS:REQ:0102	50

GENCAB:HW-SSS:REQ:0103	51

GENCAB:HW-SSS:REQ:0104	51

GENCAB:HW-SSS:REQ:0105	55

GENCAB:HW-SSS:REQ:0106	37

GENCAB:HW-SSS:REQ:0107	47

GENCAB:HW-SSS:REQ:0108	48

GENCAB:HW-SSS:REQ:0109	48

GENCAB:HW-SSS:REQ:0110	63

GENCAB:HW-SSS:REQ:0111	84

GENCAB:HW-SSS:REQ:0113	74

GENCAB:HW-SSS:REQ:0114	74

GENCAB:HW-SSS:REQ:0115	75

GENCAB:HW-SSS:REQ:0116	59

GENCAB:HW-SSS:REQ:0118	64

GENCAB:HW-SSS:REQ:0119	64

GENCAB:HW-SSS:REQ:0120	65

GENCAB:HW-SSS:REQ:0121	41

GENCAB:HW-SSS:REQ:0122	42

GENCAB:HW-SSS:REQ:0123	59

GENCAB:HW-SSS:REQ:0124	42

GENCAB:HW-SSS:REQ:0125	81

GENCAB:HW-SSS:REQ:0126	81

GENCAB:HW-SSS:REQ:0127	82

GENCAB:HW-SSS:REQ:0128	52

GENCAB:HW-SSS:REQ:0129	53

GENCAB:HW-SSS:REQ:0130	53

GENCAB:HW-SSS:REQ:0131	82

GENCAB:HW-SSS:REQ:0132	83

GENCAB:HW-SSS:REQ:0133	75

GENCAB:HW-SSS:REQ:0134	43

GENCAB:HW-SSS:REQ:0135	43

GENCAB:HW-SSS:REQ:0136	44

GENCAB:HW-SSS:REQ:0137	44

GENCAB:HW-SSS:REQ:0138	87

GENCAB:HW-SSS:REQ:0139	36

GENCAB:HW-SSS:REQ:0140	61

GENCAB:HW-SSS:REQ:0141	62

GENCAB:HW-SSS:REQ:0142	60

GENCAB:HW-SSS:REQ:0143	77

GENCAB:HW-SSS:REQ:0144	46

GENCAB:HW-SSS:REQ:0145	38

GENCAB:HW-SSS:REQ:0146	38

GENCAB:HW-SSS:REQ:0147	54

END OF DOCUMENT